Section VI-C: Special Provisions to the Standard Specifications (SPSS)

TABLE OF CONTENTS

VOLUME-II: Tunnel Facilities

SECTION 5000. TUNNEL FACILITIES

(1)	GENERAL	50-1

(2)	QUALITY CONTROL	50-5

(3)	COMMISSIONING	50-6

(4)	OPERATION/MAINTENANCE/REPARATION SERVICES	50-8

5100.	TUNNEL POWER SUPPLY SYSTEM	50-9

(1)	Application	50-9

(2)	Facility Structure	50-9

(3)	Applicable Standards	50-9

(4)	Basic Requirements	50-10

(5)	Power Distribution Equipment	50-11

(6)	Facility Structure	50-12

(7)	Device Specifications	50-15

(8)	Independent Generator Facility	50-31

(9)	Monitoring Control Format	50-36

(9)	Spare Items / Accessories	50-39

(10)	Tests and Inspections	50-40

5200.	TUNNEL LIGHTING SYSTEM	50-42

(1)	Description	50-42

(2)	Tunnel Lighting	50-42

(3)	Led Modules For Tunnel Lighting	50-47

(4)	Tunnel Lighting Led Module Controllers	50-49

(5)	Connecting Road Lighting (Entrance Lighting)	50-52

(6)	LED MODULES FOR ROAD LIGHTING	50-58

(7)	 Led Module Control Units for Road Lighting	50-60

(8)	Inspections	50-64

5300.	EMERGENCY FACILITIES	50-65

(1)	Description	50-65

(2)	Tunnel Entrance Warning Signs (Dl Board)	50-65

(3)	Tunnel Entrance Warning Signs (EL) Board	50-75

(4)	Monitoring Control Panel	50-84

(5)	Emergency Telephone	50-90

(6)	Evacuation Guidance Display/Display Lights	50-95

(7)	Quality Management	50-100

5400.	REMOTE MONITORING AND CONTROL SYSTEM	50-100

(1)	Description	50-100

(2)	Basic Requirements	50-101

(3)	Monitoring Control Equipment	50-102

(4)	FM Radio Rebroadcasting System (Including Loudspeaker Equipment)	50-116

(5)	VHF Radio Auxiliary Equipment (Including VHF Radio For Road Administrator)	50-131

(6)	CCTV CAMERA EQUIPMENT	50-144

(7)	Test, Installation and Trial Operation	50-155

(8)	Spare Parts	50-156

5500.	TUNNEL VENTILATION SYSTEM	50-157

(1)	General	50-157

(2)	Basic Requirements	50-160

(3)	Ventilation Control Equipment	50-162

(4)	Jet Fan Equipment	50-170

(5)	Measuring Equipment	50-173

(6)	Spare Parts	50-177

(7)	INSPECTION AND TESTING ADJUSTMENTS	50-178

5600.	TUNNEL FIRE FIGHTING SYSTEM	50-183

(1)	Fire Hydrants	50-183

(2)	Exterior Water Supply Outlet	50-187

(3)	Fire Pump	50-188

(4)	Automatic Water Supply System	50-189

(5)	Water Intake Pump	50-190

(6)	Motorized Ball Valve (Inlet Valve)	50-190

(7)	Automatic Air Vent Valve	50-191

(8)	Safety Valve	50-191

(9)	Flow Regulation Valve	50-191

(10)	Disaster Prevention Reception Panel	50-192

(11)	Fire Pump Control Board	50-201

(12)	Water Intake Pump Control Board	50-205

(13)	Terminal Board	50-209

(14)	Fire Detectors	50-209

(15)	Push Button Alarms (In Emergency Phone Boxes)	50-211

(16)	Pump Start Push Button Box	50-213

5700.	DISTRIBUTION LINE	50-213

(1)	Description	50-213

(2)	Basic  Requirement	50-214

5800.	MEASUREMENT AND PAYMENT	50-214

(1)	Measurement	50-214

(2)	Payment	50-214

SECTION 5000.	TUNNEL FACILITIES

(1)	GENERAL

(1.1)	Description

This work consists of the provision and installation of the Tunnel Facilities, protection and maintenance during the construction period and the Defects Notification Period. This work also includes all testing for approval of material and equipment to be provided, test and commissioning for final reception, all ancillary and incidental works necessary to complete the following items as shown in the Drawings, and as approved by the Engineer:

Tunnel Power Supply System

Tunnel Lighting System

Tunnel Emergency Facilities

Remote Monitoring and Control System

Tunnel Ventilation System

Tunnel Fire Fighting System

(1.2)	Design-Review and Updating

These requirements shall be read and applied accordingly, and without detriment, to the requirements and provisions of Clause 4.1 “Contractor’s General Obligations” of the Conditions of Contract and any other relevant requirements of the Special Provisions to the Standard Specifications.

(a)	These works consist of the Design Review and Updating by the Contractor based on the Conceptual Design provided by the Employer. The report of the Design Review/Updating shall include also all detailed drawings, applicable technical specifications and requirements for construction and materials.

(b)	The Contractor shall be responsible for surveying, designing, manufacturing, testing of equipment/ materials at the factory, packing, transporting, maintaining, installing, integrating the test system, misadjusting and commissioning the items, which are involved in the corresponding sections or paragraphs of this Specifications, at the site.

(c)	The Contractor shall be responsible for any incidental works generated on relevant items. Drawings or specifications shall be described as the Contractor’s design review and updating being in accordance with the requirements of the standards.

(d)	Specific work-items, which are consisting the design review to be performed by the Contractor, shall be in conformity with the specifications with dimensions, content, scales, forms and functions.

(e)	Unless otherwise stipulated in the Contract, the design review and updating performed by the Contractor, and the selected manufacturer/ supplier of equipment/ materials and components shall be ensured with the following design life in the actual environmental and operational conditions:

(i)	Constructional facilities:	min. 20 years

(ii)	Work structure:	min. 50 years

(iii)	Components covering the buildings	min. 20 years

(iv)	Electrical system, lighting system:	min. 20 years

(v)	Indoor architectural items: 	min. 15 years

(f)	The Contractor shall review and update the design and construct or install the auxiliary or additional facilities which are assumed to be necessary for completing the works in accordance with the Drawings, specifications and functions requirements for the system as well as by the applicable condition by the Engineer.

(g)	The Contractor shall ensure entirely his designed systems, equipment, devices, materials and components are installed and integrated fully; besides, it should be sure that operation and maintain shall be easily and effectively conducted together with a high commercial efficiency as well as a small operational and maintaining cost.

(h)	The Contractor shall also implement the requirements to ensure that all systems, equipment, materials or components shall satisfy in terms of interference from any electrical and electronic appliances in the tunnel, though they are provided by the individual chapters of technical specifications, or the systems, equipment, materials or components of other items.

(i)	The design, dimension and material of entire structures, parts shall be reviewed to avoid any impacts of any harsh operating conditions which may create distortion, vibration that may cause unfavorable impacts to the structural integrity or operation of the equipment.

(j)	The Contractor shall do the design review/updating in conformity with the relevant environmental requirements and standards.

(k)	The Contractor is responsible to meet the requirements of the relevant authorities as well as obtain all necessary agreements and approvals from the relevant agencies, including firefighting and prevention agencies, power supply companies and others.

(l)	The Contractor is responsible for coordinating with the suppliers of equipment, devices (under this Project’s scope) to clearly know the overall design, the required software and hardware; thus, it is ensured the appropriate interface as well as the interactive information among designed systems in accordance with the description in the specifications.

(1.3)	Calculation by the Contractor

(a)	The Contractor shall prepare all calculations to justify and substantiate the reviewed/updated design of all civil, structural, mechanical, electrical, process and control works and systems for which he is responsible for the design. The calculations shall contain sufficient explanation and diagrams to enable a complete understanding without any further verbal explanations. All assumption, loadings, alternates and revisions shall be clearly documented.

(b)	Computerized calculations shall include documentation which explains clearly the applied program, terminology, conventional symbols and signs.

(c)	The Contractor shall prepare and submit a single-line diagram indicating the ratings such as capacity, etc. of every items of equipment and protection, metering or any ancillary devices in accordance with the requirements of proposed equipment. A detailed load computation shall be attached with a complete diagram and a manual accompany for each applied major item.

(d)	The Contractor shall explain and submit all calculations, drawings, data of manufacturer as well as other supporting information requested by the Engineer for review and approval of the proposed or selected materials, equipment. The Engineer has right to request full or partial submissions at any time.

(e)	Procurement and manufacturing shall not commence prior to such approval being received unless it is expressly agreed by the Engineer (so the Contractor shall remain his responsibility if the further changes are necessarily requested in such this case).

(f)	The Contractor shall submit to the Engineer, for review and approval, the full detailed design review/updating documentation and drawings in order to demonstrate that the requirements of the Specifications have been completely incorporated.

(g)	The Contractor shall submit to the Engineer, for review and approval, the necessary procedures, reports and certificates to certify that the Contractor is capable to promptly carry out the manufacture, installation and other related works.

(h)	The Contractor shall undertake design-related interface meetings, in the Site, with all of the relevant sub-contractors and suppliers in the presence of the Engineer. The purpose of these design-related interface meetings is to ensure all interface requirements have been integrated.

(i)	All submittals to be made by the Contractor shall be in accordance with the Conditions of Contract (Clause 4.1: “Contractor’s General Obligations”, Sub-Clause 1.1.6.1: “Contractor’s Documents”, and other relevant conditions) and Section 117: “Contractor’s Drawings” of these Special Provisions to the Standard Specifications.

(i)		The Contractor shall submit, for review and approval by the Engineer, an schedule for the following items and shall include respective milestone-dates into the approved Programme in accordance to Section 116: “Programme”:

Submittal No.1 of the Design Review/Updating:

Detailed Work Schedule for the systems, equipment and materials showing location, fabrication, and shipment and installation periods.

List of drawings and documents to be submitted

Preliminary Interface Information for all other Sections/Divisions.

General information on proposed software including operating systems and programming language

Submittal No.2 of the Design Review/Updating:

Detailed Interface Design among facilities in the Project

System diagram

Calculations and drawings

Diagrams connecting to systems of control, electrical, mechanical, emergency equipment, etc.

Preliminary layout of equipment rooms and the others

Layout drawings showing the routing and sizes of piping routes and electrical cables and all accessory systems

Arrangement of foundations, steel support structures, stairs and walkways.

Anchor types

Equipment colors

Functional analysis, outline of software specification, tables and drawings of operators’ screens and policy for development and construction of software.

Submittal No.2 of the Design Review/Updating:

The Contractor shall submit the final design review/updating with all supporting information and final drawings. The submittal shall contain all necessary information to permit final and efficient review by the Engineer and shall include (but is not limited to):

Final detailed drawings

Equipmment lists

Details (with all equipment/device lists and specifications) of all control systems and interfaces

Detailed design calculation sheets (mechanical, structural, electrical calculations)

Arrangement of electrical equipment and devices including computer control system

Final software including specification and user manuals

Design evaluation report

Details of assembly and installation and fixing of all system, equipment and materials

Caution plates and exit signs including symbols for signage

(2)	QUALITY CONTROL

(2.1)	Testing in Site

This Sub-Clause shall be interpreted for the Tunnel Facilities, supplementary to, and without detriment to the stipulations of Section 500: “Quality Control” of these Specifications and Sub-Clause 4.9: “Quality Assurance” and Sub-Clause 7.4: “Testing” of the Conditions of Contract, and all relevant stipulations of the Contract.

(a)	All equipment, devices, units, components, and parts, which are delivered and installed under the Contract, shall be tested, inspected and certified prior to the acceptance in accordance with the requirements of the Standards, and as approved by the Engineer.

(b)	In accordance with the Specifications, the Contractor shall demonstrate that all requirements described in the Contract are satisfactorily complied.

Details of all complied documents and procedures shall be submitted to the Engineer for review and approval before each execution stage is commenced.

(c)	For the off-the-shelf or routinely manufactured equipment, the Contractor may submit a test result report or the manufacturer’s test and inspection certificate instead of an in-factory test (being exempted). In addition, the Contractor shall submit the factory's routine testing procedures to the Engineer for review and acceptance.

For the equipment or components requiring special order or specifically designed and manufactured for this project, the Contractor shall submit to the Employer proposed factory test items and test procedures for review and approval as soon as the System Design is accepted.

The Contractor shall notify in advance of each factory test to be undertaken.

After each test, upon the Engineer’s approval on the test results, the Contractor can start transporting equipment to the Site. The devices which are detected to have defects or been produced inconsistent with the standards, shall be rejected and replaced immediately on the Contractor’s expenses and responsibility.

(2.2)	Factory Test

The testing cost shall cover cost for providing all facilities, tools, labor, consumable parts, measuring apparatus and appliances required in connection for all inspection and tests at factory or on the manufacturer's premises, and all other expenses. Separate payment of these cost will not be made,

The Contractor shall state the location of factory test for the test items in his Technical Proposal.

The locations where the factory test is conducted shall have the necessary facility, testing device, measuring apparatus, recording system, power supply and other arrangements to conduct the test items listed in the Test Procedure. The Contractor shall state specifically the in-situ facility and equipment tests as well as the required measurement tools or devices applied into these tests at the proposed locations in his technical proposal.

(2.3)	Inspection

All equipment shall be inspected before delivery and upon arrival at the site. The inspection shall be performed with the following items:

Painted surfaces and color

Assembling conditions

Design and dimensions

Part setting

Wiring within the cabinet

Damages during transportation

(3)		COMMISSIONING

This Sub-Clause shall be interpreted for the Tunnel Facilities, supplementary to, and without detriment to the stipulations of Subsection 509: “Acceptance Tests for Completed Works or Parts of the Works”, Clause (3): “Testing and Commissioning” of these Specifications, and Clause 9: “Test on Completion” and Sub-Clause .4: “Testing” of the Conditions of Contract, and all other relevant stipulations of the Contract.

(3.1)	Procedure

(a)	Commissioning Test procedure shall be applied to the equipment, devices and software comprising the system including network equipment, fiber optic cable, communication and power cables, all electrical equipment installed at the required locations, adjusted and tested by the Contractor.

(b)	Commissioning Test shall be conducted at two levels; Commissioning Test for a portion of works, and Commissioning Test for the entire Works. The Commissioning Test for a portion of works shall be conducted for a group of equipment at the site that functions as a sub-system and achieves part of the system functions.

(c)	The Commissioning Test for the entire Works shall be conducted to confirm that the system supplied under the Contract complies with the Employer’s requirements, the approved specifications, the prepared drawings which have been submitted for all aspects of one system by the Contractor.

(d)	During the Commissioning the entire Works, all the functions of the equipment required under the Contract shall be tested. Data exchange between the terminal equipment and the Tunnel Control Center system will be tested including the case of the interruption and recovering the communication link between the terminal equipment in addition to the functions of respective systems. The test shall be conducted with the attendance of the Project Manager.

(e)	The Contractor shall keep a clear record of all tests conducted. The record shall include time, place, equipment, procedure, functions, persons attending, and faults or problems encountered. The test results, even if they are not satisfactory, shall be documented.

(f)	The Employer will provide electricity free of charge to the Contractor for the purpose of conducting Commissioning Test if permanent electrical supply is available. Otherwise, the Contractor shall arrange electricity, water and gas necessary for the Commissioning Test.

(g)	The Contractor shall prepare or arrange the test apparatus and equipment, temporary connection, testing software, test data, test vehicle, tools and other items necessary for conducting test. The cost of such items shall be included in the cost of test in the Pricing Document and no separate payment shall be made.

(3.2)	Commissioning Test for the Whole System

(a)	Procedure: The Contractor, in accordance with these Specifications and the Conditions of Contract, shall notify to the Engineer before the date of commissioning for the whole system with test items, procedure, criteria for judging the test results and test schedule.

The Contractor shall send to the Engineer the regular certified copies of the test results when the tests have been successfully completed. The Engineer, if the results satisfy the requirements, will notify the Contractor in written that the Works are ready for commissioning operations.

If any major defects are uncovered during the test, the Contractor shall prepare and submit to the Engineer, for reviewing and approval, a proposal to remedy the defects including a method statement and all necessary technical details. The Contractor shall not take corrective actions before the proposed solution have received the Engineer’s approval. Minor faults and defects detected during the Commissioning procedure may be corrected during the trial operation period upon the Engineer’s acceptance.

“Major defects” might cause, among others, the following results:

Lose data, erroneous data or inconsistency in operation;

Low quality of data acquisition such as missing observation or delay in observation;

Low quality of local/ remote control such as no response or delay of response;

Unexpected shutdown or halt of operation;

Failure to changeover to backup equipment; and

Failure to restart and resume the operation after power recovery of the device that is designed to have such function.

Worsen the situation of other defects which were initially classified as minor defect.

(b)	Test on Completion: Testing and Commissioning shall be in accordance with the Clause: “Test on Completion” of the Conditions of Contract and all related conditions of these specifications and the Contract.  The Taking Over Certificate shall be issued in accordance with Clause 10: “Employer’s Taking Over” of the Conditions of Contract upon the duly compliance on the requirements for “Test Completion”.

(c)	Trial Operation Time: Trial operation shall be conducted for two (2) months after Taking-Over Certificate has been issued for the respective works. The operation of the system will be carried out by the Employer or his designated operator. Should any critical or major defect be found during the trial operation, the trial operations shall restart after rectification of the defects are approved by the Engineer.

In such case, the Employer based on the evaluation made by the Engineer, can apply the following:

- Repetition of the trial period, and consequent extension of the Defects Notification Period in accordance to Clause 11.3: “Extension of Defects Notification Period” of the Conditions of Contract; or

- Application of Clause 11.4: Failure to Remedy Defects” of the Conditions of Contract.

For minor defects, the Contractor shall rectify it to the satisfaction of the Engineer and the trial operation will continue without interruptions.

(4)	OPERATION/MAINTENANCE/REPARATION SERVICES

(a)	The Contractor has be responsible of providing operation, maintenance and reparation services for all equipment, systems and work items during warranty period, as mentioned in related chapters of these Specifications.

(b)	Proposal of the Contractor for operation, maintenance and reparation services shall be updated and developed to comprehensive operation, maintenance and reparation program.

(c)	Operation, maintenance and reparation services provided by the Contractor including:

(i)	Assign skilled staffs to support the Employer in operation of machines, equipment and systems during warranty period.

(ii)	Periodical and annual testing and maintenance procedures in regulated time in approved Operation and Maintenance manuals, including checking of system, equipment and machines, calibration, cleaning and greasing for all couplings to avoid incidents by any reason .

(iii)	Immediate reparation service including capacity of reparation after receiving orders from the Employer or the Engineer.

(iv)	Supply spare-part equipment, grease, oil

(d)	In case the reparation, maintenance or other external services are necessary due to excessive use, misuse or other reasons out of control of the Contractor. The Contractor shall provide external service for maintenance, reparation and all cost shall be paid by the Employer.

(e)	The Contractor still have responsibility for the effectiveness and optimization of system operation

(f)	All maintenance and reparation services implemented by the Contractor or local agencies and established officially under the responsibility of the Contractor, certified or authorized to provide service of the Contractor and manufacturing factories of specified system, equipment or related woks. The reparation and maintenance implemented by such organization is legal.

(g)	All reparation, maintenance, operation services shall be implemented with the witness of the Employer representative for the operation and maintenance training.

5100.	TUNNEL POWER SUPPLY SYSTEM

(1)	Application

This list of specifications specifies electrical equipment to supply, and the equipment for each device for step-down conversion from the NEA 11kV power supply. An independent generator facility, DC power supply, and uninterruptible power supply are also included to secure safe operation of tunnel facilities during times of NEA power outages.

(2)	Facility Structure

The power distribution equipment comprises the following facilities.

East-side high voltage electrical room, electrical room facilities (including DC power supply uninterruptible power supply), generator room

East-side independent generator room (including underground fuel tank)

West-side high voltage electrical room, electrical room facilities (including DC power supply, uninterruptible power supply)

(3)	Applicable Standards

These facilities abide by the laws and standards below.

(a) Electricity Business Act

(b) Japanese Industrial Standards (JIS)

(c) Japan Electric Committee Standards (JEC)

(d) Japan Electrical Manufacturers’ Association (JEM)

(e) Japan Land Engine Manufacturers’ Association (LES)

(f) Independent Generator Facility Earthquake Resistance Design Guidelines (NEGA)

In addition, the following laws and standards will be applied. However, these specifications should be given priority.

Applicable Standards

Seven Design Essentials Electrical Facilities Electrical Facilities Chapter 1, Power Distribution Equipment (NEXCO RI July 2017)

Seven Design Essentials Electrical Facilities Electrical Facilities Chapter 2, Independent Generator Facilities (NEXCO RI July 2017)

Seven Design Essentials Electrical Facilities Electrical Facilities Chapter 3, DC Power Supply and Uninterruptible Power Supply (NEXCO RI, July 2017

Electronic Telecommunications Facility Design Guidelines/Explanation (Electric Facilities) 2017 version The Telecommunications Association

Electronic Telecommunications Facility Installation Standard Diagrams January 2015. The Telecommunications Association

Facility Equipment Specifications Manual Electricity Power Distribution Equipment Standard Specifications Manual. July 2017 (NEXCO-RI)

Facility Equipment Specifications Manual Electricity Independent Generator FacilityStandard Specifications Manual July 2017 (NEXCO-RI)

These facilities must be manufactured, installed, tested, and commissioned under a quality guarantee and quality management system meeting ISO 9001 standards. The manufacturer must be an organization which possesses ISO 9001 certification from an independent public body.

(4)	Basic Requirements

(a)	Basic Design

The power distribution equipment will receive 11kV50Hz power from NEA via two lines near the east-side electrical room, and these lines will run into the east-side high voltage electrical room. The boundary of responsibility for NEA jurisdiction will be installed at the two switchgear panels near the east-side electrical room, and the interior sector switchgear (DS) will be the primary NEA cable bed. The high voltage electrical room will comprise 12kV switchgear and a transformer board for step-down conversion of 11kV to 400V. The 400V electricity will be supplied to the electrical room, where it will be converted to either 220V or 110V as needed to supply power for each piece of equipment. The status of each device can be monitored from the front of the switchgear and cubicle, and the necessary signals will connect to a control system device through the relay terminal board, to enable monitoring control.

Backup power for use during NEA power outages is provided according to facility importance level. Circuits are classified into general circuits (AC), independent generator circuits (GC) and important circuits (INV).

(Note):

AC circuits	go offline during NEA power outages.

GC circuits	supplied with power from the independent generator facility during NEA power outages

INV circuits	reverse-switch to DC power during the period required to switch from NEA power to independent generator facility power during NEA power outages. Prevents momentary blackouts to keep the power supply stable.

(b)	Reliability

This system will run 24 hours a day, 365 days a year. Devices which can bear up to sustained use will be employed.

(c)	Extensibility

Extensibility will be made possible, to promote ease of future expansions and repairs. It will be made easy to add basic facilities, etc.

(5)	Power Distribution Equipment

This item will be applied to devices installed as part of power supply control facilities (hereinafter, “the facilities.”)

Equipment Outline:

(a) 	Use Locations

The equipment will be used in the east-side electrical room and west-side electrical room, and will be indoor devices.

However, the east-side sectional switchgear will be an outdoor device.

(b)	Surrounding Conditions

Temperature:	Indoor	0°C to +40°C

- Outdoor	-10°C to +40°C

Humidity	Indoor	10% to 85% RH.

- However, this assumes no condensation.

(6)	Facility Structure

(a)	Device List:

Table 51-1 shows the list of devices included in the power distribution equipment for Eastern Side Electrical Room:

Table 51-1: Power Distribution Equipment in Eastern Side Electrical Room

| Item | Details | Qty. | Unit | Comments |
| --- | --- | --- | --- | --- |
| Sectional Switchgear (1) | DS LA | 1 | Panel | Outdoor type |
| Sectional Switchgear (2) | DS LA | 1 | Panel |  |
| Draw-In Board (1) Circuit A | DS | 1 | Panel |  |
| Power Receiving Panel (1): Circuit A | CB×1 | 1 | Panel |  |
| Draw-In Board (2) Circuit B | DS | 1 | Panel |  |
| Power Receiving Panel (2): Circuit B | CB×1 | 1 | Panel |  |
| Ventilation Transformer (1): Primary Panel/ Ventilation Transformer (2): Primary Panel | CB×2 | 1 | Panel |  |
| Lighting Transformer Primary Panel/ West-Side Electrical Room Power Sending Panel (1) Circuit A | CB×1 | 1 | Panel |  |
| Bus Tie Panel (1) | CB×1 | 1 | Panel |  |
| Bus Tie Panel (2) | CB×1 | 1 | Panel |  |
| Independent Generator Tie Panel/ West-Side Electrical Room Power Sending Panel (2) : Circuit B | CB×2 | 1 | Panel |  |
| Independent Generator Power Transfer Panel | DT-DS | 1 | Panel |  |
| West-Side Electrical Room , Power Sending Panel ; Independent Generator Circuit /Maintenance Power Panel | CB×2 | 1 | Panel |  |
| West-Side Electrical Room Power Sending Transfer Panel | DT-DS | 1 | Panel |  |
| Ventilation Transformer Panel (1) | Tr 300kVA | 1 | Panel |  |
| Ventilation Transformer Secondary Panel (1) | MCCB | 1 | Panel |  |
| Ventilation Transformer Panel (2) | Tr 300kVA | 1 | Panel |  |
| Ventilation Transformer Secondary Panel (2) | MCCB | 1 | Panel |  |
| Lighting Transformer Panel | Tr 300kVA | 1 | Panel |  |
| Lighting Transformer Secondary Panel | MCCB | 1 | Panel |  |
| Auxiliary Transformer Panel (1) | Tr 75kVA | 1 | Panel |  |
| Auxiliary Transformer Panel (2) | Tr 50kVA | 1 | Panel |  |
| Lighting Control Panel |  | 1 | Panel | Including light sensor and automatic light adjustment device |
| Tunnel Lightning Panel (1) | MCCB | 1 | Panel |  |
| Tunnel Lightning Panel (2) | MCCB | 1 | Panel |  |
| Uninterruptible Power Supply Device | 30 kVA 100Ah/ 180 Cell | 1 | Set |  |
| Controller DC Power Supply Device | 50Ah/ 54 Cell | 1 | Set |  |
| Maintenance Transfer Panel No.1 No.2 |  | 1 | Panel |  |
| Ground Terminal Board |  | 1 | Panel |  |
| Telecommunications Equipment Room Distribution Panel |  | 1 | Panel |  |
| Ventilation Control Center (1) | 2 units installed | 1 | Panel |  |
| Ventilation Control Center (2) | 2 units installed | 1 | Panel |  |

Table 51-2 shows the list of devices included in the power distribution equipment for Western Side Electrical Room:

Table 51-2: Power Distribution Equipment in Western Side Electrical Room

| Item | Details | Qty. | Unit | Comments |
| --- | --- | --- | --- | --- |
| West-Side Electrical Room |  |  |  |  |
| Draw-In Board (1) Circuit A | DS | 1 | Panel |  |
| Power Receiving Panel (1) Circuit A | CB×1 | 1 | Panel |  |
| Draw-In Board (2) Circuit B | DT-DS | 1 | Panel |  |
| Power Receiving Panel (2) Circuit B | CB×1 | 1 | Panel |  |
| Maintenance Power Supply Panel | CB×1 | 1 | Panel |  |
| Ventilation Transformer (1) Primary Panel/ Ventilation Transformer (2); Primary Panel | CB×2 | 1 | Panel |  |
| Lighting Transformer Primary Panel/ Road Station; Power Sending Panel | CB×2 | 1 | Panel |  |
| Bus Tie Panel | CB×1 | 1 | Panel |  |
| Ventilation Transformer Panel (1) | Tr 300kVA | 1 | Panel |  |
| Ventilation Transformer Secondary Panel (1) | MCCB | 1 | Panel |  |
| Ventilation Transformer Panel (2) | Tr 300kVA | 1 | Panel |  |
| Ventilation Transformer Secondary Panel (2) | MCCB | 1 | Panel |  |
| Lighting Transformer Panel | Tr 300kVA | 1 | Panel |  |
| Lighting Transformer Secondary Panel | MCCB | 1 | Panel |  |
| Auxiliary Transformer Panel (1) | Tr 75kVA | 1 | Panel |  |
| Auxiliary Transformer Panel (2) | Tr 75kVA | 1 | Panel |  |
| Lighting Control Panel |  | 1 | Panel | Including light sensor and automatic light adjustment device |
| Tunnel Lightning Panel (1) | MCCB | 1 | Panel |  |
| Tunnel Lightning Panel (2) | MCCB | 1 | Panel |  |
| Uninterruptible Power Supply Device | 20 kVA 100Ah/ 180 Cell | 1 | Set |  |
| Controller DC Power Supply Device | 50Ah/ 54 Cell | 1 | Set |  |
| Maintenance Transfer Panel No.1 No.2 |  | 1 | Panel |  |
| Ground Terminal Board |  | 1 | Panel |  |
| Ventilation Control Center (1) | 2 units installed | 1 | Panel |  |
| Ventilation Control Center (2) | 2 units installed | 1 | Panel |  |

(b)	Device Design

The designs for the devices and equipment are detailed below:

(i)	All devices are “indoor use” except when specified otherwise.

(ii)	The shape of the housing for high-voltage devices must be JEM1425 “High Voltage Metal Closed-Type Switchgear,” conforming to the standards in the table below.

(iii)	The shape of the housing for low-voltage devices must be JEM1265 “Low Voltage Metal Closed-Type Switchgear,” conforming to the standards in the table below.

| Power Distribution Panel Type | Format ※1 | Standard |
| --- | --- | --- |
| Draw-In Panel | CY | JEM 1425 |
| Power Receiving Panel | CX | JEM 1425 |
| Transformer Primary Panel | CX | JEM 1425 |
| Power Transfer (DS) Panel | CY | JEM 1425 |
| Main Transformer Panels | CY | JEM 1425 |
| Transformer Secondary Panel | CX | JEM 1425 |
| Low Voltage Power Panel | CY CX | JEM 1425 |
| Low Voltage Lighting Panel | CY CX | JEM 1425 |
| Low Voltage Maintenance Transfer Panel | CX | JEM 1425 |

※1 The low-voltage maintenance transfer panel is assumed to be a free-standing panel.

First format letter: 	M: Metal-Clad Type Switchgear

- C: Cubicle-Type Switchgear

Second format letter: 	W: Pull-Out-Type Device

- X: Fixed-Type Device

- Y: Carry-Out Type

(iv) 	The control center for the jet fan must be a “JEM 1195 Control Center” series model, and all models of the same structure and rated values must be compatible.

In addition, all sides must have a door for each unit, and the back must have a hooking cover or door.

The phase-advancing condenser will be housed inside the panel.

(v) 	All sides of the high voltage power distribution panel must have doors, and the back side must have a hooking cover or door.

(vi) 	Materials for the high-voltage and low-voltage panels must have capacities exceeding those of a steel sheet (hot rolled steel sheet) or equivalent item.

(c)	Temperature Increase

Temperature increase inside the panels and within each device must meet the compliance standards mentioned in the previous item detailing ambient conditions, and must be within a range that does not interfere with any of the components.

(7)	Device Specifications

(a)	East-Side Electrical Room Switchgear

(i)	Section Switch Box (1)(2)

Format	Outdoor Closed Free-Standing Type

Quantity	2 panels

Equipment Stored in Main Panel (per 1 panel):

①	Surge Arrester	14kV  5kA  3 pc.

②	Circuit Breaker	3P DS 12kV 1200A 25kA  1 unit

③	Voltage Detector	11kV 1 Phase Detection

1 set with detector, controller, voltmeter

④	Other necessary items	as required

(ii) 	Draw-In Board (1) Circuit A Draw-In Board (2) Circuit B

Format	Indoor Unit Closed Free-Standing Type

Quantity	2 panels

Equipment Stored in Main Panel (per 1 panel):

① 	Single-Throw Circuit Breaker	3P DS 12kV 1200A 25kA  1 unit

② 	Other necessary items	as required

(iii)	Power Receiving Panel (1) Circuit A Power Receiving Panel (2) Circuit B

Format	Indoor Unit Closed Free-Standing Type

Quantity	2 panels

Equipment Stored in Main Panel (per 1 panel):

① 	High Voltage Vacuum Circuit Breaker	12kV 630A 25kA draw-out type	  1 unit

② 	Gauge Transformer	11kV/110V molded type draw-out type	 2 units

③	Current Transformer	200/5A molded type

2 units

④	Other necessary items	as required

(iv)	Ventilation Transformer (1) Primary Panel / Ventilation Transformer (2) Primary Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	High Voltage Vacuum Circuit Breaker	12kV 630A 25kA

draw-out type  1 unit each

②	Current Transformer	20/5A molded type  3 units each

③	Other necessary items	as required

(v)	Lighting Transformer Primary Panel / West-Side Electrical Room Power Sending Panel (1) Circuit A

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

① 	High Voltage Vacuum Circuit Breaker	12kV 630A 25kA draw-out type  	1 unit each

② 	Current Transformer	20/5A molded type

3 units each

③ 	Other necessary items	as required

(vi) 	Bus Tie Panel (1) Bus Tie Panel (2)

Format	Indoor Unit Closed Free-Standing Type

Quantity	2 panels

Equipment Stored in Main Panel (per 1 panel)

①	High Voltage Vacuum Circuit Breaker	12kV 630A 25kA draw-out

type  1 unit

②	Gauge Transformer	11kV/110V molded type draw-out type

2 units

③	Other necessary items	as required

(vii)	Independent Generator Tie Panel / West-Side Electrical Room Power Sending Panel (2) Circuit B

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel

① 	High Voltage Vacuum Circuit Breaker	12kV 630A 25kA draw-out type  	1 unit each

② 	Current Transformer	100/5A molded type

3 units

③ 	Other necessary items	as required

(viii) 	Intendent Generator Power Transfer Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity		1 panel

Equipment Stored in Main Panel:

①	Double-Throw Circuit Breaker: 3P DT-DS 12kV 1200A 25kA 1 unit

②	Other necessary items	as required

(ix)	West-Side Electrical Room Power Sending Panel Independent Generator Circuit/Maintenance Power Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	High Voltage Vacuum Circuit Breaker	12kV 630A 25kA draw-out type 	 1 unit each

②	Current Transformer	100/5A  15/5Amolded type

3 units each

③	Other necessary items	as required

(x)	West-Side Electrical Room Power Sending Transfer Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Double-Throw Circuit Breaker: 3P DT-DS 12kV 1200A 25kA  1 unit

②	Other necessary items	as required

(xi)	Ventilation Transformer Panel (1)

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 unit

- Format: molded type (with short-proofing panel)

- Capacity: 300kVA

- Primary Voltage	three-phase three-wire : 11000V  50Hz

- Secondary Voltage : three-phase three-wire ; 460V 50Hz

- Connection System: Star (Y) and Delta (Δ) Connection

- Accessories: dial thermometer (with alarm contact), anti-vibration rubber, wheels

②	Other necessary items	as required

(xii)	Ventilation Transformer Secondary Panel (1)

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Gauge Transformer	440/110V molded type  2 units

②	Current Transformer	600/5A molded type  2 units

③	Surge Arrester	480V 2.5kA  3 units

④	Molded Case Circuit Breaker	1 set

⑤	Knife Switch	3P 100A  1 unit

⑥	Other necessary items	as required

(xiii)	Ventilation Transformer Panel (2)

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel

①	Three-Phase Transformer	1 unit

- Format: molded type（with short-proofing panel）

- Capacity: 300kVA

- Primary Voltage: three-phase three-wire 11000V 50Hz

- Secondary Voltage: three-phase three-wire 415V 50Hz

- Connection System: Star (Y) and Delta (Δ) Connection

- Accessories: dial thermometer (with alarm contact), anti-vibration rubber, wheels

②	Other necessary items	as required

(xiv)	Ventilation Transformer Secondary Panel (2)

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Gauge Transformer	440/110V molded type  2 units

②	Current Transformer	500/5A molded type  2 units

③ Surge Arrester	480V 2.5kA  3 units

④ Molded Case Circuit Breaker	1 set

⑤ Knife Switch	3P 100A  1 unit

⑥ Other necessary items	as required

(xv)	Lighting Transformer Panel

Format		Indoor Unit Closed Free-Standing Type

Quantity		1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 unit

- Format: molded type（with short-proofing panel）

- Capacity: 300kVA

- Primary Voltage: three-phase three-wire 11000V 50Hz

- Secondary Voltage: three-phase three-wire 415V 50Hz

- Connection System: Star (Y) and Delta (Δ) Connection

- Accessories: dial thermometer (with alarm contact), anti-vibration rubber wheels

② Other necessary items	as required

(xvi)	Lighting Transformer Secondary Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel

① Gauge Transformer	440/110V molded type  2 units

② Current Transformer	500/5A molded type  2 units

③ Surge Arrester	480V 2.5kA  3 units

④ Molded Case Circuit Breaker	1 set

⑤ Knife Switch	3P 100A  1 unit

⑥ Other necessary items	as required

(xvii)	Auxiliary Transformer Panel (1)

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

① Three-Phase Transformer	1 unit

- Format: molded type

- Capacity: 75kVA

- Primary Voltage: three-phase three-wire 415V 50Hz

- Secondary Voltage: three-phase three-wire 220V 50Hz

- Connection System: Star (Y) and Delta (Δ) Connection

- Accessories: anti-vibration rubber, wheels

②	Other necessary item	1 set

(xviii)	Auxiliary Transformer Panel (2)

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 unit

- Format: molded type

- Capacity: 50kVA

- Primary Voltage: three-phase three-wire 415V 50Hz

- Secondary Voltage: single-phase two-wire 220V 50Hz

- Connection System: Scott connection

- Accessories: anti-vibration rubber, wheels

②	Other necessary items	as required

(xix)	Lighting Control Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Automatic Light Modulation Device

(with light senses)  	1 set

②	Light Modulation Transformer	1 unit

③	Other necessary items	as required

(xx)	Tunnel Lightning Panel (1) (2)

Format	Indoor Closed Free-Standing Type

Quantity	2 panels

Equipment Stored in Main Panel

①	Zero-Phase Current Transformer	1 set

②	MCCB	1 set

③	Earth Fault Overcurrent Circuit Breaker	1 set

④	Other necessary items	as required

(xxi)	Maintenance Transfer Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Molded Case Circuit Breaker		1 set

②	Gauge Transformer	440/110V molded type	1 unit

③	Double-Throw Circuit Breaker	1 set

④	Other necessary items	as required

(xxii)	Ventilation Control Center Panel (1)

Format	Indoor Closed Free-Standing Type

Quantity	1 panel (2 units installed)

Equipment Stored in Main Panel:

①	Zero-Phase Current Transformer	1 set

②	MCCB	1 set

③	Earth Fault Overcurrent Circuit Breaker	1 set

④	Phase-Advancing Condenser	1 set

⑤	Other necessary items	as required

(xxiii)	Ventilation Control Center Panel (2)

Format	Indoor Closed Free-Standing Type

Quantity	1 panel (2 units installed)

Equipment Stored in Main Panel:

① Zero-Phase Current Transformer	1 set

② MCCB	1 set

③ Earth Fault Overcurrent Circuit Breaker	1 set

④ Phase-Advancing Condenser		1 set

⑤ Other necessary items	as required

(xxiv)	Telecommunications Equipment Room Distribution Panel

Format	Indoor Wall Mounted Type (with cable duct)

Quantity	1 panel

Equipment Stored in Main Panel:

①	Molded Case Circuit Breaker	1 set

②	Other necessary items	as required

(b)	East-Side Electrical Room DC Power Supply

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Three-Phase Rectifier	1 unit

- Format        thyristor with automated constant-voltage device

- Capacity       30A

②	Lead-Acid Battery	1 set

- Format	control valve seal type (MSE Type)

- Capacity	50Ah

- No. of Cells	54 Cells

③	Silicon Dropper	20A  1 set

④	Other necessary items	as required

(c)	East-Side Electrical Room Uninterruptible Power Supply Device

(i)	Input/output Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 set

- Format	dry-type

- . Capacity	30KVA  10kVA

②	Molded Case Circuit Breaker	1 set

③	Other necessary items	as required

(ii)	Battery Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Lead-Acid Battery	1 set

- Format	control valve seal type (MSE type)

- Capacity	100Ah

- No. of Cells	180 Cells

②	Other necessary items	as required

(iii)	Inverter Panel

Format: Indoor Closed Free-Standing Type

Quantity: 1 panel

Equipment Stored in Main Panel:

①	Three-Phase Inverter	1 unit

- Format: continuous inverter power supply system

- Capacity: 30kVA

- Element: GPT Element   High-Frequency PWM Inverter

②	Converter	1 unit

- Format: high-efficiency converter type

- Capacity: 150(A)

- Element: IGBT Element   High-Frequency PWM Inverter:

③	Molded Case Circuit Breaker		1 set

④	Electromagnetic Contactor		1 set

⑤	Current Transformer		/5A  1 set

⑥	Other necessary items		1 set

(d)	West-Side Electrical Room Switchgear

(i)	Draw-In Board (1) Circuit A

Format: Indoor Unit Closed Free-Standing Type

Quantity:  panel

Equipment Stored in Main Panel:

①	Single-Throw Circuit Breaker 3P DS 12kV 1200A 25kA

1 unit

②	Other necessary items	as required

(ii)	Draw-In Board (2) Circuit B

Format: Indoor Unit Closed Free-Standing Type

Quantity: 1 panel

Equipment Stored in Main Panel:

①	Single-Throw Circuit Breaker: 3P DT-DS 12kV 1200A 25kA

1 unit

②	Other necessary items	as required

③	Main Panel Mounting Equipment:

(iii)	Power Receiving Panel (1) Circuit A Power Receiving Panel (2) Circuit B

Format	Indoor Unit Closed Free-Standing Type

Quantity	2 panels

Equipment Stored in Main Panel (per 1 panel)

①	High Voltage Vacuum Circuit Breaker 12kV  630A  25kA

draw-out type 	1 unit

②	Gauge Transformer	11kV/110V  molded type

draw-out type  	2 units

③	Current Transformer	100/5A  molded type

2 units

④	Other necessary items	as required

(iv)	Maintenance Power Supply Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	High Voltage Vacuum Circuit Breaker: 12kV  630A  25kA  draw-out type  	1 unit

②	Current Transformer: 15/5Amolded type	  3 units

③	Other necessary items	as required

(v)	Ventilation Transformer (1) Primary Panel / Ventilation Transformer (2) Primary Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	High Voltage Vacuum Circuit Breaker	12kV  630A  25kA  draw-out type  	1 unit each

②	Current Transformer: 20/5A molded type	3 units each

③	Other necessary items	as required

(vi)	Lighting Transformer Primary Panel / Backup Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

① 	High Voltage Vacuum Circuit Breaker: 12kV  630A 25kA  draw-out type 	1 unit each

② Current Transformer: 20/5A molded type 	3 units each

③ Other necessary items	as required

(vii)	Bus Tie Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	High Voltage Vacuum Circuit Breaker: 12kV  630A  25kA  draw-out type  	1 unit

②	Gauge Transformer: 11kV/110V  molded type  draw-out type

2 units

③	Other necessary items	as required

(viii)	Ventilation Transformer Panel (1)

Format: Indoor Unit Closed Free-Standing Type

Size: Quantity	1 panel

Equipment Stored in Main Panel

①	Three-Phase Transformer	1 unit

- Format	molded type (with short-proofing panel)

- Capacity	300kVA

- Primary Voltage	three-phase three-wire 11000V 50Hz

- Secondary Voltage	three-phase three-wire 460V 50Hz

- Connection System	Star (Y) and Delta (Δ) Connection

- Accessories	dial thermometer (with alarm contact), anti-vibration rubber, wheels

②	Other necessary items	as required

(ix)	Ventilation Transformer Secondary Panel (1)

Format: Indoor Closed Free-Standing Type

Quantity: 1 panel

Equipment Stored in Main Panel:

①	Gauge Transformer: 440/110V  molded type

2 units

②	Current Transformer: 600/5A  molded type  	2 units

③	Surge Arrester: 480V  2.5kA  	3 units

④	Molded Case Circuit Breaker		1 set

⑤	Knife Switch	3P 100A  1 unit

⑥	Other necessary items	as required

(x)	Ventilation Transformer Panel (2)

Format: Indoor Unit Closed Free-Standing Type

Quantity: 1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 unit

- Format	molded type (with short-proofing panel)

- Capacity	300kVA

- Primary Voltage	three-phase three-wire 11000V 50Hz

- Secondary Voltage	three-phase three-wire 415V 50Hz

- Connection System	 Star (Y) and Delta (Δ) Connection

- Accessories	dial thermometer (with alarm contact), anti-vibration rubber, wheels

②	Other necessary items	as required

(xi)	Ventilation Transformer Secondary Panel (2)

Format: Indoor Closed Free-Standing Type

Quantity: 1 panel

Equipment Stored in Main Panel:

①	Gauge Transformer: 440/110V molded type

2 units

②	Current Transformer: 500/5A  molded type

2 units

③	Surge Arrester: 480V  2.5kA  	3 units

④	Molded Case Circuit Breaker		1 set

⑤	Knife Switch	3P 100A  1 unit

⑥	Other necessary items	as required

(xii)	Lighting Transformer Panel

Format: Indoor Unit Closed Free-Standing Type

Quantity: 1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 unit

- Format	molded type (with short-proofing panel)

- Capacity	300kVA

- Primary Voltage	three-phase three-wire 11000V 50Hz

- Secondary Voltage	three-phase three-wire 415V 50Hz

- Connection System	Star (Y) and Delta (Δ) Connection

- Accessories	dial thermometer (with alarm contact), anti-vibration rubber, wheels

②	Other necessary items	as required

(xiii)	Lighting Transformer Secondary Panel

Format: Indoor Closed Free-Standing Type

Quantity: 1 panel

Equipment Stored in Main Panel:

①	Gauge Transformer: 440/110V  molded type

2 units

②	Current Transformer: 500/5A  molded type

2 units

③ Surge Arrester: 480V  2.5kA  	3 units

④ Molded Case Circuit Breaker	1 set

⑤ Knife Switch: 3P 100A  	1 unit

⑥ Other necessary items	as required

(xiv)	Auxiliary Transformer Panel (1)

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 unit

- Format	molded type

- Capacity	75kVA

- Primary Voltage	three-phase three-wire 415V 50Hz

- Secondary Voltage	three-phase three-wire 220V 50Hz

- Connection System	Star (Y) and Delta (Δ) Connection

- Accessories	anti-vibration rubber, wheels

②	Current Transformer: 250/5A molded type

2 units

③	Zero-Phase Current Transformer	1 set

④	Earth Fault Overcurrent Circuit Breaker	  1 set

⑤	Other necessary items	as required

(xv)	 Auxiliary Transformer Panel (2)

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 unit

- Format	molded type

- Capacity	50kVA

- Primary Voltage	three-phase three-wire 415V 50Hz

- Secondary Voltage	single-phase two-wire 220V 50Hz

- Connection System	Scott connection

- Accessories	anti-vibration rubber, wheels

②	Current Transformer: 150/5A molded type

2 units each

③	Zero-Phase Current Transformer	1 set

④	Earth Fault Overcurrent Circuit Breaker	1 set

⑤	Other necessary items	as required

(xvi)	Lighting Control Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Automatic Light Modulation Device (with light sensor)

1 set

②	Light Modulating Transformer	1 unit

③	Molded Case Circuit Breaker	1 set

④	Single-Throw Electromagnetic Contactor	1 set

⑤	Zero-Phase Current Transformer	1 set

⑥	Earth Fault Overcurrent Circuit Breaker	1 set

(xvii)	Tunnel Lightning Panel (1) (2)

Format	Indoor Closed Free-Standing Type

Quantity	2 panels

Equipment Stored in Main Panel

①	Zero-Phase Current Transformer	1 set

②	MCCB	1 set

③	Earth Fault Overcurrent Circuit Breaker	1 set

④	Other necessary items		1 set

(xviii)	Ventilation Control Center Panel (1)

Format	Indoor Closed Free-Standing Type

Quantity	1 panel (2 units installed)

Equipment Stored in Main Panel

①	Zero-Phase Current Transformer	1 set

②	MCCB	1 set

③	Earth Fault Overcurrent Circuit Breaker	1 set

④	Phase-Advancing Condenser	1 set

⑤	Other necessary items	as required

(xix)	Ventilation Control Center Panel (2)

Format	Indoor Closed Free-Standing Type

Quantity	1 panel (1 unit installed)

Equipment Stored in Main Panel

①	Zero-Phase Current Transformer	1 set

②	MCCB		1 set

③	Earth Fault Overcurrent Circuit Breaker   	1 set

④	Phase-Advancing Condenser	1 set

⑤	Other necessary items		1 set

(xx)	Maintenance Transfer Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Molded Case Circuit Breaker	1 set

②	Gauge Transformer: 440/110V  molded type

1 unit

③	Double-Throw Circuit Breaker	1 set

④	Other necessary items	as required

(xxi)	Ground Terminal Panel

Format	Indoor Wall-Mounted Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Ground Terminal Plate	1 set

②	Auxiliary Electrode Terminal for Measurement	2 pc.

③	Other necessary items	as required

(e)	West-Side Electrical Room DC Power Supply

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Three-Phase Rectifier	1 unit

- Format: thyristor with automated constant-voltage device

- Capacity: 30A

②	Lead-Acid Battery	1 set

- Format	control valve seal type (MSE type)

- Capacity	50Ah

- No. of Cells	54 Cells

③	Silicon Dropper: 20A  	1 set

④	 Molded Case Circuit Breaker  	1 set

⑤	Other necessary items	as required

(f)	West-Side Electrical Room Uninterruptible Power Supply Device

(i)	Input/output Panel

Format	Indoor Closed Free-Standing Type

Size	900W×1000D×2350H

Quantity	1 panel

Equipment Stored in Main Panel:

①	Three-Phase Transformer	1 set

- Format	dry-type

- Capacity	20KVA

②	Molded Case Circuit Breaker  	1 set

③	Other necessary items	as required

(ii)	Battery Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Lead-Acid Battery	1 set

- Format	control valve seal type (MSE type)

- Capacity	100Ah

- No. of Cells	180 Cells

②	Other necessary items	as required

(iii)	Inverter Panel

Format	Indoor Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

① 	Three-Phase Inverter	1 unit

- Format	continuous inverter power supply system

- Capacity	20kVA

- Element	IGBT Element High-Frequency PWN Inverter

②	Converter	1 unit

Format	High-Efficiency Converter Format

Capacity	100(A)

Element	IGBT Element High-Frequency PWN Inverter

③	Molded Case Circuit Breaker 	 1 set

④	Electromagnetic Contactor  	1 set

⑤	Current Transformer	/5A  1 set

⑥	Other necessary items	as required

(8)	Independent Generator Facility

(a)	Equipment Outline

(i)	Location

The usage location shall be the east-side generator room, and an indoor model shall be used.

(ii)	Ambient Conditions

Temperature: 
indoor	0°C -to +40°C

- outdoor	-10°C to +40°C

Humidity:

- indoor	10% to 85%RH

- However, this assumes no condensation.

(b)	Facility Structure

The independent generator facility will consist of the following items:

| Item | Unit | Qty | Comments |
| --- | --- | --- | --- |
| AC Generator | Unit | 1 | 625kVA, 3ø 3W 11kV 50Hz, 4P 1500min-1 |
| Diesel Engine | Unit | 1 | 546kW, radiator cooling, light oil or electric start-up |
| Generator Panel | Panel | 1 | VCB, EVT, CT |
| Automatic Start-Up Panel | Panel | 1 | EXTR, AVR, auxiliary circuit |
| Start-Up DC Power Supply | Set | 1 | DC 24V 200Ah |
| Exhaust Muffler | Unit | 1 | 85dB(A) attached to generator |
| Fuel Transfer Pump | Unit | 1 | 0.75kW |
| Fuel Tank | Unit | 1 | 900 liters |
| Fuel Supply Box | Panel | 1 | SUS-made outdoor, wall-mounted |
| Vent Fan | Unit | 2 | 85dB(A), fan 5.5kW, damper, anti-insect net on hood |
| Exhaust Duct | Unit | 1 | With damper and hood |

(c)	Device Structure

Device designs are stipulated as follows:

(i)	All devices shall be “indoor type” unless specified otherwise.

(ii)	The shape of the housing for high-voltage devices must be JEM1425 “High Voltage Metal Closed-Type Switchgear,” conforming to the standards in the table below.

| Panel Type | Format | Standard |
| --- | --- | --- |
| Generator Panel | CW | JEM 1425 |

First format letter:	C: Cubicle-Type Switchgear

Second format letter:	W: Pull-Out-Type Device	X: Fixed-Type Device

Y: Carry-Out Type

The panel material must have capacities exceeding steel sheet (hot rolled steel sheet) or the equivalent.

(iii)	Devices and power distribution wires must be heat-resistant so as not to be affected by heat generated by the motor, and must be firmly affixed. The motor and generator must include anti-vibration rubber or similar measures to absorb vibration.

(iv)	The engine must include a device exceeding the capacities of the lubricating oil pump, and the sliding portion and moving parts of the lubricating oil supply nozzle must not cause a breakage in the oil film when switched off.

(v)	The devices must be coated or painted to prevent rust. Pipes must be painted the same color as the generator. Once the pipes are painted, a color stripe shall be painted at the entrance/exit of the pipe, along with an arrow indicating the direction of the flow through the pipe. Furthermore, the surface of pipes to be buried in the outdoor pit must be painted to prevent rust.

(vi)	All components of devices, etc. must meet or exceed JIS standards, and effort should be made to increase reliability of all devices by using a standard for components that exceeds actual usage conditions by as much as possible.

In addition, anti-explosive designs must also be compatible with these standards.

(vii)	These devices must provide a stable supply of electricity to each type of load system.

(viii)	The earthquake resistance of the facilities must satisfy the “heavy machinery A” standard set forth in the Japanese Ministry of Land, Infrastructure, Transport, and Tourism “Electronic and Telecommunication Facilities Construction General Specification Manual, Chapter 3 – Earthquake Resistance Standards.”

(ix)	To prevent movement and falls during earthquakes, items equipped with anchor bolts and anti-shake devices selected based on earthquake engineering calculations must include anti-quake stoppers.

(x)	Radiator shutters must automatically open during diesel engine operation and close when operation is stopped.

Dimensions must fit the radiator-equipped independent generator facility structure, and not impede exhaust.

(xi)	Meters must be included to measure the following operational conditions.

Rotation or frequency of the internal combustion engine.

Lubricating oil pressure on the internal combustion engine. (However, for items which supply lubricating oil through a forced circulation system, it must be possible to change to measuring lubricating oil amount or lubricating oil surface.)

Lubricating oil temperature in the internal combustion engine (however, for items which operate based on the temperature of the water used to cool the lubricating oil, it must be possible to change to measuring the temperature of the cooling water.)

Cooling water temperature in the internal combustion

(xii)	Silencers must satisfy area noise regulations, and must be designed so as not interfere with the performance of the motor.

(d)	Device Specifications

(i)	Independent Generator Device (Package)

The independent generator device must be a low-noise cubicle type (85dB(A)).

(ii)	AC Generator

Format	three-phase projective type synchronous generator

Rated Output	625kVA

Rated Voltage and Frequency: three-phase three-wire type, 11kV, 50Hz

No. of Poles and RPM:  4 poles, 1500 rpm (1/min)

Power Factor	80% (delayed)

Excitation System	brushless excitation system

Running Time	continuous, more than 24 hours

(ii)	Diesel Engine

4-cycle water cooled vertical direct injection type

Output	more than 546kW

Rotations	1500rpm

Start-Pp Mechanism:  electric start-up

Start-Up Time	within 10-40 seconds

Cooling Format	radiator cooling (built-in type)

Fuel	light oil

Run Time	more than 72 hours

Accessories: common bed (with anti-vibration device), priming pump, no. of rotations, lubricating oil thermometer, lubricating oil pressure gauge, cooling water thermometer, exhaust thermometer, cooling water heater, oil pan heater, oil tank heater, canvas duct, other necessary items

(iv)	Generator Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	High Voltage Vacuum Circuit Breaker: 12kV  630A  25kA

1 unit

②	Excitation Transformer	1 unit

③	Grounding Gauge Transformer: 11kV/110V/110/3V

1 unit

④	 Current Transformer	100/5A  3 units

⑤	Current Limiting Resistor	1 set

⑥	Filter	1 set

⑦	Other necessary items	as required

(v)	Automatic Start-Up Panel

Format	Indoor Unit Closed Free-Standing Type

Quantity	1 panel

Equipment Stored in Main Panel:

①	Automatic Voltage Regulator	1 set

②	Molded Case Circuit Breaker	1 set

③	Electromagnetic Contactor	1 set

④	Other necessary items	as required

(vi)	Start-Up DC Power Supply

Format	Indoor Unit Closed Free-Standing Type

Size	Quantity	 1 panel

Equipment Stored in Main Panel:

①	Three-Phase Rectifier	1 unit

- Format	thyristor with automated constant-voltage device

- Capacity	20A

②	Lead-Acid Battery	1 set

- Format	control valve seal type (MSE type)

- Capacity	200Ah

- Voltage	DC 24V

③	Molded Case Circuit Breaker	1 set

④ 	Other necessary items	as required

(vii) 	Exhaust Muffler

Format	ceiling-suspended type

Quantity	1 unit

Sound Level	less than 85 dB (A) 1 m from exhaust vent

(viii)	Fuel Transfer Pump

Format	motor direct-coupled

Quantity	2 units

Mouth Diameter	20mm

Discharge Amount	31L/min

Suction Lift	3 m

Electric Motor	0.75kW three-phase three-wire 220V 50Hz. Safety anti-explosive type

(ix)	Fuel Tank

Format	steel plate, frame mounted type

Quantity	1 unit

Capacity	900L

Accessories	oil level detection device (anti-explosive), oil level gauge, frame, ladder, wing pump, other necessary items

(x)	Fuel Supply Box

Format	outdoor wall-mounted type, SUS

Size	500W×350D×450H

Quantity	1 panel

Accessories	oil level gauge (anti-explosive type), lorry earth terminal, other necessary items

(xi)	Vent Fan

Format	indoor wall-mounted type

Quantity	2 units

Sound Level	less than 85 dB (A) 1 m from air intake vent

Accessories	damper, air supply hood (SUS-made, with anti-insect net SUS mesh), other necessary items

(xii)	Exhaust Duct

Format	indoor floor type

Quantity	1 unit

Sound Level	less than 85 dB (A) 1 m from air intake vent

Accessories	damper, vent hood (SUS-made, bird protection net SUS mesh), other necessary items

(9)	Monitoring Control Format

(a)	Power Reception Control

Control is achieved through the power receiving (automatic-manual) toggle switch mounted on the power receiving panel and the remote-direct toggle switch, according to the following scheme:

(b)	Power Recovery Control

(i)	When power restoration is detected at the voltage relay (84) at the power receiving point, after being confirmed by the timer and tripping the bus-tie circuit breaker (52), the power receiving circuit breaker (52) is thrown.

(ii)	When the power receiving circuit breaker (52) is thrown, a stop order is sent to the generator simultaneously.

(c)	Action flow-chart

(d)	Lighting Control:

(i)	Control Format Switching

①	Block Diagram

Lighting control is achieved based on the following scheme, using the remote-manual toggle switch mounted on the lighting control panel, and the power receiving remote-direct share toggle switch mounted on the power receiving panel.

(ii)	Lighting Control Details

①	Individual Control

- Switch the toggle switches to “manual” and “direct,” then press the push-button switch on the front of the control center unit to achieve individual control.

- If the switches are set to “manual” and “direct,” the interlocking display light on the front of the lighting control panel will go out, and display signals will be sent as-is to the remote monitoring control facility.

(Depending on the conditions of the electromagnetic contactor)

②	Manual Interlocking Control

- Switch the toggle switches to “manual” and “remote” to achieve interlocking control, with each applicable circuit controlled by the remote monitoring control facility operations switches.

- The signal from the main electrical room lighting control panel automatic light modulation device automatically controls the entrance lights on the main electrical room side, while the signal from the auxiliary electrical room lighting control panel automatic light modulation device automatically controls the entrance lights on the auxiliary electrical room side.

- Basic lighting is controlled by interlocking control for the east-side electrical room and the west-side electrical room.

- Automatic light modulation device operation chart

(9)	Spare Items / Accessories

Spare items and accessories listed below are in addition to the spare items stipulated in the manufacturer standard set.

(a)	Spare Items

(i)	Power Distribution Equipment

| No. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
| 1 | Fuses | 100% |  |
| 2 | Bulbs for Signal Lights | 100% | LED |
| 3 | Globes for Signal Lights | 20% |  |
| 4 | In-Panel Fluorescent Lamp | 100% |  |

(ii)	DC Power Supply / Uninterruptible Power Supply

| No. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
| 1 | Fuses | 100% |  |
| 2 | Bulbs for Signal Lights | 100% | LED |
| 3 | Globes for Signal Lights | 20% |  |

(Note) No. of devices is the number of devices per electrical room.

(iii)	Independent Generator Facility

| No. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
| 1 | Rubber Seals | 1 set |  |
| 2 | Fuses | 100% |  |
| 3 | Bulbs for Signal Lights | 100% (note) | LFD |
| 4 | Globes for Signal Lights | 20% |  |

(b)	Accessories

(i)	Power Distribution Transforming Equipment

| No. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
| 1 | Breaker Lifter | 1 unit |  |
| 2 | Breaker Handle | 1 pc. |  |
| 3 | Transformer Draw Rail | 1 unit |  |
| 4 | Test Terminal Plug | 1 set | For VT and CT |
| 5 | Protection Relay Plug | 1 set |  |
| 6 | Door Handle Key | 3 pc. |  |
| 7 | Breaker Operation Handle | 1 pc. |  |

(Note) No. of devices is the number of devices per electrical room.

(ii)	DC Power Supply / Uninterruptible Power Supply

| No. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
| 1 | Spanner | 1 pc. | For storage battery terminal connection |
| 2 | Accessory Storage Box | 1 pc. |  |

(Note) No. of devices is the number of devices per electrical room.

(iii)	Independent Generator Facility

| No. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
| 1 | Standard Tools | 1 set | With storage box |
| 2 | Test Terminal Plug | 1 set | For VT and CT |
| 3 | Protection Relay Plug | 1 set |  |
| 4 | Door Handle Key | 1 pc. |  |
| 5 | Breaker Draw Rail | 1 unit |  |
| 6 | Breaker Handle | 1 pc. |  |

(10)	Tests and Inspections

(a)	Independent Inspection

The devices used in the facilities must be subject to an independent inspection including all the tests below at the factories where they are manufactured, and the results of the inspections must be submitted for review.

(i)	Power Distribution Equipment

External Inspection

Mechanism Operation Test

Sequence Test

Insulation Resistance Test (Voltage Resistance Test)

Interface Test

Phase Sequence

(ii)	DC Power Supply / Uninterruptible Power Supply

External Inspection

Mechanism Operation Test

Sequence Test

Insulation Resistance Test (Voltage Resistance Test)

Characteristics Test

Interface Test

(iii)	Independent Generator Facility

The devices used in the facilities must be subject to an independent inspection including all the tests below at the factories where they are manufactured, and the results of the inspections must be submitted for review.

External Inspection

Startup Test

Load Test

①	1/4 load	20 minutes

②	2/4 load	20 minutes

③	3/4 load	20 minutes

④	4/4 load	2 hours

⑤	11/10 load	30 minutes

Generator Bearing Temperature Measurement

Governor Test

Overspeed Proof Test

Sequence Test (including test of the protection devices)

Mechanism Operation Test

Insulation Resistance Test (Voltage Resistance Test)

(b)	On-Site Inspection

Once construction on the site is complete, the following on-site inspections shall be performed, and the results shall be submitted for review.

(i) 	Transformers

External Inspection

Mechanism Operation Test

Sequence Test

Main Circuit Insulation Resistance Test

High-Voltage Element Voltage Resistance Test

Ground Resistance Measurement

Phase Sequence

(ii)	DC Power Supply / Uninterruptible Power Supply

The same inspections shall be performed as were performed as independent inspections, and the results of the inspections shall be submitted for review.

(iii)	Independent Generator Facility

Once construction on site has finished, the following on-site inspections shall be performed, and the results of the inspections shall be submitted for review.

The inspections shall be performed on the same items as for the independent inspections.

If a request for a report is received from a concerned party institution, the following inspections shall be conducted and the results submitted for review.

Underground fuel tank and fuel use tank leakage inspection

Fuel pipe pressure inspection

(c)	General Operation Tests

When on-site inspections are finished, all facilities must be subject to commissioning as a whole, and adjusted if necessary.

Power Distribution Equipment Internal General Operation Tests

Counter Test with Monitoring Control Facilities

5200.	TUNNEL LIGHTING SYSTEM

(1)	Description

Tunnel lighting shall be mounted on tunnel walls, using the format detailed below to ensure that the interior of the tunnel is well-lit, thereby contributing to traffic safety.

Lighting will be installed in the connecting evacuation tunnels to ensure an evacuation route in case of emergency.

Basic Lighting

Entrance Lighting

Special Structure Lighting (Emergency Parking Strip, Etc.)

Backup Lighting for Power Outages

Lighting shall be installed outside the tunnel entrances and exits to illuminate the width of the road and changes in road path and surface, etc.

(2)	Tunnel Lighting

(a)	Applicable Standards

Each device must meet the standards below and conform to these specifications.

Electrical Appliances and Materials Safety Act

The Ministerial Ordinance on Technical Standards for Electrical Equipment

Japanese Industrial Standards (JIS)

JIS C 8105-1:2013	Lighting Components – Part 1: General Safety Requirement Rules

JIS C 8105-2-3:2011	Lighting Components – Parts 2-3: Safety Requirements for Road and Highway Lighting Components

JIS C 8105-3:2011	Lighting Components – Part 3: General Capacity Requirement Rules

JIS C 8105-5:2014	Lighting Components – Part 5: Luminous Intensity Measurement Methods JIS C 8153:2009

Applicable Standards

Seven Design Essentials Electrical Facilities Electrical Facilities Chapter 4, Road Lighting Facilities. (NEXCO RI July 2017)

Seven Design Essentials Electrical Facilities Electrical Facilities Chapter 5, Tunnel Lighting Facilities (NEXCO RI July 2017)

Electronic Telecommunications Facility Design Guidelines / Explanation (Electric Facilities) 2017 version. The Telecommunications Association

Electronic Telecommunications Facility Utility Standard Diagrams January 2015. The Telecommunications Association

(b)	Equipment Specifications

LED lamps shall be used for tunnel lighting facilities. These lamps use LEDs as a light source and comprise the following components: LED tunnel light fixtures, LED modules, LED module controllers.

(c)	Tunnel Lighting Fixtures

(i)	Fixture Design

LED lamps used for tunnel lighting facilities use LEDs as a light source and comprise the following components: LED tunnel light fixtures, LED modules, LED module controllers.

(d)		Fixture Types

Fixture types are shown in Table 52-1.

Table 52-1: LED Tunnel Lighting Fixture Types

| Type | Fixture Format | Rated Luminosity | Mass |
| --- | --- | --- | --- |
| Side Wall Mounted Type For Basic Lighting | White LED (LED108) | > 13,550 lm | <15kg |
|  | White LED (LED36） | > 4,500 lm |  |
| Side Wall Mounted Type For Entrance Lighting | White LED (LED40) | > 6,100 lm |  |
|  | White LED (LED60) | > 9,050 lm |  |
|  | White LED (LED80) | > 12,050 lm |  |
|  | White LED (LED120) | > 18,100 lm |  |
|  | White LED (LED160) | > 24,150 lm |  |
|  | White LED (LED200) | > 30,200 lm |  |
|  | White LED (LED240) | > 36,250 lm |  |
|  | White LED (LED280) | > 42,250 lm |  |

Note. The lowest rated luminosity value is more than 90% of the value shown in the table. All components shall be luminosity-adjustable.

(e)		General Structure

(i)	Shared Characteristics

Fixtures shall be enclosed, durable, waterproof, corrosion-resistant, and easy to inspect. Therefore, they should be able maintain their mechanical, electrical, and luminescent functions during normal operation.

Protection against the intrusion of solid, waterborne, or airborne dust and dirt shall abide by a standard of JIS C 8105-1:2013 IP55 at minimum. Damage from solid, waterborne, or airborne dust and dirt must be prevented.

Both the fixtures and the mounting brackets must have the highest corrosion resistance rating, and include prevention measures against interstitial rust and electrolytic corrosion caused by contact between different metals.

The front surfaces of fixtures shall be free of fasteners (screws, bolts, nuts) which could impede cleaning.

In principle, mounting brackets should be made of the same metal as the fixtures to be mounted, but if the metals are of different types, measures against electrolytic corrosion must be installed.

The housing for LED modules, reflecting plates, lenses, etc. must be designed to minimize the possibility of intrusion by solid dust and dirt particles which could decrease the luminescence of the components.

(ii) Design, Materials, and Parts

Fixture design and main materials and parts are listed as follows.

Main Body:

The main body of fixtures shall be made of aluminum or extruded aluminum alloy meeting the JIS H 4100 standard, or die-cast aluminum alloy meeting the JIS H5202 standard, or die-cast aluminum alloy meeting the JIS H 5302, and the main body of the fixtures should have a strength rating greater than or equal to stainless steel plate with a standard material thickness of 1.0mm (SUS304).

Mounting Brackets:

Mounting brackets shall be made of JIS G 4305 standard cold-rolled stainless-steel plate (SUS304) with a standard thickness of at least 4.0mm.

Translucent Covers:

Translucent covers shall have strength and translucency ratings compatible with JIS R 3206:2014 tempered glass with a standard thickness of at least 4.0 mm. The optical performance of components must be fully sustainable, and must be impervious to scratches, cracks, and clouding which could impede performance.

Reflecting Plates and Lenses:

Control of light distribution of LED modules shall be achieved with reflecting plates, lenses, or a combination of the two. If reflecting plates are used, they must be molded to JIS H 4000:2014 “aluminum and aluminum alloy plate and strip” standard, or molded from resin, and must be at least as durable as surface-treated material. If lenses are used, they must be molded from resin with maximum heat resistance and durability, or similar. The combined LED modules, reflecting plates or lenses, and translucent covers must fully maintain their optical performance.

Seals:

Seals must be highly elastic and heat-resistant, must not absorb moisture, and must be resistance to deterioration.

Internal Wiring:

All connections to internal wiring of fixtures shall use crimp terminals.

Cable Glands:

Cable glands shall be made of waterproof composite resin.

Nameplates:

Nameplates should not be easily removable.

(iii) Fall Prevention

Fixture bodies shall include support hardware at the left and ride of the top side, so that stainless wires can be inserted as a fall-prevention measure.

(iv) Coating

Fixture bodies shall be preprocessed by degreasing, etc., then bake-coated with at least one layer of composite resin, with equivalent strength, rust and corrosion resistance.

(f)	Optical Performance

Fixtures shall have sufficient optical performance to effectively illuminate the surface of the road and tunnel walls while mounted on the side walls of the tunnel. They shall be measured using the methods stipulated in JIS C 8105-5:2014, and must satisfy the capacity indices laid out in 5. Performance Requirements.

The lighting utilization factor shall be calculated based on the values measured according to the method stipulated in JIS C 8105-5:2014, and must be greater than or equal to the values shown in Table 52-2.

Light output ratio must be at least 80% of the values for the conditions stipulated in JIS C 8105-5:2014 for ambient temperatures of -10 to 40° C.

Table 52-2: Lighting Utilization factor

| Type | Fixture Format | Angle Direction | Lighting Utilization Factor at Vertical Angle from Reference Axis |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 10° | 20° | 30° | 40° | 50° | 60° |
| Side Wall Mounted Type For Basic Lighting | White LED (LED108) White LED (LED36) | Vehicle Lane | 0.12 | 0.29 | 0.47 | 0.57 | 0.59 | 0.60 |
|  |  | Sidewalk | 0.09 | 0.16 | 0.23 | 0.29 | 0.34 | 0.37 |
| Side Wall Mounted Type For Entrance Lighting | White LED (LED40) - White LED (LED280) | Vehicle Lane | 0.19 | 0.36 | 0.46 | 0.48 | 0.49 | 0.50 |
|  |  | Sidewalk | 0.19 | 0.35 | 0.44 | 0.46 | 0.47 | 0.48 |

Reference Axis, Vertical Angle, Direction (Vehicle Lane Side/Sidewalk Side)

(g)	Insulation Resistance

Must satisfy the capacities when measured according to the method standardized in JIS C 8105-1:2013.

(i)	When tested as detailed in (2), insulation resistance must be greater than or equal to 5 MΩ. Also, when tested in the cold, it must be greater than or equal to 30 MΩ.

(ii)	For the insulation resistance test, lamps must be lit continuously until all parts of the fixture have reached roughly the same temperature. Then, the insulation resistance of both terminals and the non-charging metal parts must be measured with a 500 V Insulation Resistance Meter or other instrument with greater precision, as standardized in JIS C 1302:2014 “Insulation Resistance Meter.”

(h)	Voltage Resistance

Must satisfy the capacities in (1) when measured according to the method standardized in JIS C 8105-1:2013.

(i)	Voltage resistance must withstand the voltage delivered when tested as detailed in (2).

(ii)	The voltage resistance test must be conducted directly after the insulation resistance test, sending a test voltage (2U+1000 V) close to a sign wave of 50 Hz or 60 Hz in frequency between the charged parts and non-charged parts for about one minute, and checking that no abnormalities occur.

(i)	Thermal Shock Resistance

The thermal shock resistance of fixtures must satisfy (1) at the time of testing using the JIS C 8105-2-3:2011 standard method.

(i)	When thermal shock resistance is tested according to (2), the fixture exterior and translucent cover must not crack, warp, or break.

(ii)	For the thermal shock resistance test, the fixture should be illuminated as it would be for normal use, until all parts of the fixture have reached roughly the same temperature. At this point, water 10 °C colder than the surrounding temperature shall be poured on the translucent cover to simulate rain for the test. However, the simulated rainwater should be no colder than 4°C.

(j)	Spare Items

Fuse  100%

(3)	Led Modules For Tunnel Lighting

(a)	Types and Applicable Regulations

The following standards shall be applied to LED modules for road lighting, along with these specifications.

JIS C 8152-2:2014	White Lighting Luminous Diode (LED) Measurement Methods, Part 2:

LED modules and LED light engines

JIS C 8154:2009	General Lighting LED Modules – Safety Specifications

JIS C 8155:2010	General Lighting LED Modules – Required Performance

(b)	LED Module Performance

LED modules shall be contained within fixtures with a protection class rating of at least IP55, as standardized in JIS C 8105-1:2013 “Lighting Components – Lighting Components – Part 1: General Safety Requirement Rules,” and shall be designed for appropriate heat dissipation to maintain the standard luminous flux continuously over the long term.

The initial characteristics of the combined module and module control device must satisfy Table 52-3, and shall also conform the requirements of Clause 5 5 Connecting Road Lighting for lighting equipment.

Table 52-3: LED Module Initial Characteristics (Total Luminous Flux)

| Type | Initial Characteristics (Rated Value) |  |
| --- | --- | --- |
|  | Correlated Color Temperature (K) | Average Color Rendering Index Ra |
| White LED for Lighting | 4500±2000 | > 60 |

(c)	LED Module Lifespan

(i)	Lifespan

The total illumination time elapsed before the LED modules illuminated according to standard conditions cease to illuminate, or the total illumination time elapsed before their luminous flux falls below 80% of the value (LED module standard luminous flux) measured at initial illumination (regarded as non-lighting) shall be compared, and the shorter of the two-time spans shall be considered the lifespan of the LED modules.

(2)	Rated Lifespan

The published average value for the time elapsed until the survival rate calculated based on the number of units which have ceased to function in a group of LED modules of the same type manufactured at the same time falls to 50% shall be considered the rated lifespan, and the value is shown in Table 52-4.

Alternatively, in addition to manufacturer testing, rated lifespan can be estimated logically based on the LED unit manufacturer’s LED operation conditions specifications for temperature and current, the technical data showing the change over time of the optical performance maintenance rate, the LED element temperature depending on the condition of the fixture, etc.

Table 52-4: Rated Lifespan of LED Modules

| Type | Rated Lifespan (h) |
| --- | --- |
| White LED for Lighting | > 90,000 |

Fixtures must be engineered for heat dissipation at greater than or equal to the value shown in Table 52-4, and LED modules must be selected accordingly.

(iii)	Method for Calculating Lifespan

LED module lifespan testing must be conducted according to JIS C 8155:2010 Appendix C (Luminous Flux Maintenance Test and Lifespan Test Illumination Conditions).

The estimated lifespan of LED modules must be calculated using one of the methods below.

Value estimated using Illuminating Engineering Society of North America (IES) LM-80 (Luminous Flux Maintenance Rate Measurement Method) and TM-21 (Long-Term Luminous Flux Maintenance Rate Estimation Method)

Lifespan value estimated from the Arrhenius plot of temperature acceleration test results based on the use temperature. Lifespan estimation conditions shall be set as a fixture ambient temperature of 30 °C, with normal rated current flowing to the LED modules mounted in the fixture.

(4)	Tunnel Lighting Led Module Controllers

(a)	Types and Applicable Regulations

The following standards shall be applied to LED module controllers for road lighting, along with these specifications.

JIS C 8147-1:2011	Lamp Controllers - Part 1: General Rules and Safety Requirements

JIS C 8147-2-13:2014	Lamp Controllers - Part 2-13:

Individual Requirements for LED Module Controllers for DC or AC Power Supply

JIS C 8153:2009	LED Module Controllers – Performance Requirements

JIS C 61000-3-2:2011	Electromagnetic Compatibility – Part 3-2: Limit Value – Harmonic Current Generation Limit Value

(Device with input current of less than 20A per phase)

JIS C 61000-4-5:2009	Electromagnetic Compatibility－Part 4-5: Testing and Measuring Technology – Surge Immunity Testing

(b)	LED Module Controller Performance

(i)	Design and Materials

Design and materials shall be in accordance with JIS C 8147-2-13:2014.

(ii)	Dimensions

LED module controllers should be of the right dimensions to be housed within the fixture body, and should be mounted with consideration for fixture heat dissipation, etc.

(iii)	Lead Wires

Lead wires must have capacities equivalent to JIS C 3317:2000 “Grade heat-resistant polyvinyl chloride insulated wires”, JIS C 3306:2000 “vinyl cord” or JIS C 3327:2000 “600V rubber cabtyre cable” and must have a nominal cross-sectional area of at least 0.75 mm2.

(iv)	Performance

LED Module controllers must have sufficient power supply capacity for the LED modules in their light fixture.

LED module controllers shall be contained within fixtures with a protection class rating high than IP55, as standardized in JIS C 8105-1:2013 “Lighting Components – Part 1: General Safety Requirement Rules,” so as to withstand long-term use.

LED Module controllers must have the capacity to stably supply electricity at the maximum level used by the LED modules, and must function to protect the LED modules by suppressing excess current, etc.

(v)	Characteristics of LED Module Controllers for Basic Lighting

The circuit power factor for LED module controllers shall be at least 90% (for full illumination), and should be designed to minimize input power.

Rated input current for LED module controllers shall be AC415V.

The main characteristics of LED module controllers for basic lighting are shown in Table 52-5.

Table 52-5: Characteristics of LED Module Controllers for Basic Lighting

| Component Format | Rated Input Voltage (V) | Rated Input Current (A) | Rated Electricity Consumption (W) | Power Factor (%) |
| --- | --- | --- | --- | --- |
| White LED (LED108) | 415 | < 0.26 | < 102 | > 90 |
| White LED (LED36) |  | < 0.10 | < 36 |  |
| White LED (LED40) |  | < 0.12 | < 45 |  |
| White LED (LED60) |  | < 0.17 | < 65 |  |
| White LED (LED80) |  | < 0.21 | < 85 |  |
| White LED (LED120) |  | < 0.33 | < 129 |  |
| White LED (LED160) |  | < 0.41 | < 169 |  |
| White LED (LED200) |  | < 0.53 | < 213 |  |
| White LED (LED240) |  | < 0.62 | < 254 |  |
| White LED (LED280) |  | < 0.74 | < 299 |  |

Note 1: Rated input current and rated electricity consumption values are for the end of lifespan (after 90,000 hours have elapsed).

(vi)	Noise Characteristics

Noise terminal voltage from the light fixtures and noise power from the light fixtures must satisfy the performance listed below when measured by the method stipulated in the Electrical Appliances and Materials Safety Act.

Terminal Voltage	526.5 kHz - 5 MHz: < 56 dB

- 5 MHz - 30 MHz: < 60 dB

Noise Power	30 MHz - 300 MHz: < 55 dB

(vii)	Harmonic Current

Relative limit values for fixtures whose active input power exceeds 25 W (Class C: lighting devices) shall be less than those standardized in JIS C 61000-3-2 :2011.

Table 52-6: Relative Limit Values for Class C Devices

| Harmonic Degree n |  | Maximum Permissible Harmonic Currents as a Percentage of Light Fixture Fundamental Harmonic Input Current (%) |
| --- | --- | --- |
| Even Harmonics | 2 | 2 |
| Odd Harmonics | 3 | 30×λ Note) |
|  | 5 | 10 |
|  | 7 | 7 |
|  | 9 | 5 |
|  | 11≦n≦39 | 3 |

Note: λ indicates circuit power factor

(viii)	Surge Protection

Surge protection must be greater than or equal to that necessary for voltage loads of 4 kV for common mode (ground) and 2kV for normal mode (wire), as standardized for class 4 conditions in JIS C 61000-4-5:2009.

(ix)	Initial Luminous Flux Correction

A function must be included which automatically adjusts excess brightness at the time of installation to a standard brightness level (at least 80% of the rated luminous flux value). The initial luminous flux correction method shall be automatic, using light sensors to measure the interior brightness of the light fixtures, or using program control.

(xi)	Light Adjustment Function

The basic lighting level must be adjustable such that lighting is 1/2 during nighttime and 1/4 during daytime, and such that entrance lighting level is 3/4 in sunny weather, 1/2 in level I cloudy weather, and 1/4 in level 2 cloudy weather.

Light adjustment control shall be achieved via a timer or light adjustment signal from the lighting control panel.

(c)	LED Module Control Device Lifespan

(i)	Lifespan

The total illumination time elapsed before the LED module controllers operating under standard conditions either break, or their output falls below the rated value and they become unusable, shall be considered the lifespan of the LED module controllers.

(ii)	Rated Lifespan

The average value for the time elapsed until the lifespan survival rate of a group of LED module controllers of the same type manufactured at the same time falls to 50% shall be considered the rated lifespan, and the value is shown in Table 52-7.

Table 52-7: LED Module Control Device Rated Lifespan

| Type | Rated Lifespan (h) |
| --- | --- |
| White LED for Road Lighting | > 90,000 |

Circuits must be designed and parts selected such that components housed within fixtures for use may operate for longer than their rated lifespan.

(ii)	Lifespan Calculation Method

The manufacturer shall report to the client on the basis for the engineered lifespan of the LED module controllers, achieved using one of the methods below.

Lifespan shall be estimated under conditions of a set fixture ambient temperature of 30 °C.

Lifespan value estimated from the Arrhenius plot of temperature acceleration test results based on the use temperature

Lifespan value estimated based on calculations using the maximum temperature derating factor, etc. for the main components used

Value calculated using lifespan value estimated via a method standardized by the LED module control device manufacturer and ambient temperature conditions during actual installation

(5)	Connecting Road Lighting (Entrance Lighting)

The LED road illumination light fixtures use LEDs as a light source, and are composed of LED road light fixtures, LED modules, and LED module controllers.

(a)	Applicable Standards

The following standards shall be applied to LED module controllers for road lighting, along with these specifications.

JIS C 8147-1:2011	Lamp Controllers - Part 1: General Rules and Safety Requirements

JIS C 8147-2-13:2014	Lamp Controllers - Part 2-13: Individual Requirements for LED Module Controllers for DC or AC Power Supply

JIS C 8153:2009	LED Module Controllers – Performance Requirements

JIS C 61000-3-2:2011	Electromagnetic Compatibility – Part 3-2: Limit Value – Harmonic Current Generation Limit Value

(Device with input current of less than 20A per phase)

JIS C 61000-4-5:2009	Electromagnetic Compatibility－Part 4-5:

Testing and Measuring Technology – Surge Immunity Testing

(b)	Road Lighting Equipment Specifications

Fixture type is shown in Table 52-8.

Table 52-8: LED Road Lighting Fixture Type

| Type | Fixture Type | Rated Luminous Flux |
| --- | --- | --- |
| Pole-Head Type | White LED Road Light Fixture | > 14,700 lm |

Note 1: The type is specified in JIS C 8105-2-3; 2: Must be at least 90% of the minimum rated luminous flux value.

(c)		Structure

Fixtures must be durable, waterproof, weather resistant, and corrosion resistant, and maintenance inspections must be easy to conduct. During normal operations, mechanical, electrical and optical functions must be continuously sustained.

(i)	Fixture Geometry and Mass

Fixture geometry is not expressly stipulated, but the pressure-receiving area must be less than 0.14 m2 from the front direction and less than 0.15 m2 from the side, and the mass must be less than 10 kg.

Values outside of these standard values must be checked using the prescribed calculations in JIL 1003：2009 “Light Pole Strength Calculation Standards.”

(ii)	Junction with Light Pole

A ø60.5 ×120 adapter shall be used for the junction with the light pole, and the fixture must be designed to prevent rotation or falling due to vibrations, etc.

(iii)	Protection from the Intrusion of Solid Dust and Dirt Particles and Water Droplets

Protection shall be greater than or equal to a standard of JIS C 8105-1：2013 IP23 (equivalent to conventional rain-proofing). Damage from solid, waterborne, or airborne dust and dirt must be prevented.

The housing for LED modules, reflecting plates, lenses, etc. must have a protection class greater than or equal to IP44, and designed to minimize the possibility of intrusion by solid dust and dirt particles which could decrease the luminescence of the components. In addition, if the LED module controllers are housed within the fixtures, they must have a protection class greater than or equal to IP44.

(iv) Grounding Bolts

Pole support hardware must include grounding bolts.

(v) Set Marks

The fixtures must have “set marks” which indicate the proper location for mounting at the spot where the fixture will contact the pole.

(vi)	Fixture Mounting Method

The method for mounting fixtures shall be standard linear light pole mounting, but must also be compatible with curved light pole mounting. Fixtures must be securely mounted in at least two places, (at least two bolts or at least two equivalent mountings with sufficient strength).

(vii)	Fall Prevention Design

Even if the mounting holding the fixture to the pole becomes loose, the fixture must include a fall-prevention design such that the fixture will not rotate excessively or fall off.

The fixture fall prevention design shall employ a bolt (at least M6) which passes through a hole in one side of the pole adapter, as well as a fall-prevention wire connecting the fixture to the ole and a dedicated bolt (at least M6) which can secure this wire.

(d)	Component Materials and Parts

The main materials and parts which make up the fixtures are listed below.

(i)	Main Body

The main body of fixtures shall be made of a material (including coating, if necessary) equivalent to die-cast aluminum alloy meeting the JIS H 5302:2006 standard, with a strength, anti-rust, anti-corrosion rating equivalent to ADC12, and shall not have any cavities, cracks, rust, or coating unevenness which could cause damage.

(ii)	Translucent Cover

Translucent covers shall have strength and translucency ratings compatible with JIS R 3206:2014 tempered glass with a standard thickness of at least 4.0 mm. The optical performance of components must be fully sustainable, and must be impervious to scratches, cracks, bubbles and clouding which could impede performance.

(iii)	Reflecting Plates and Lenses

Control of light distribution of LED modules shall be achieved with reflecting plates, lenses, or a combination of the two. If reflecting plates are used, they must be molded to JIS H 4000:2014 “aluminum and aluminum alloy plate and strip” standard, or molded from resin, and must be at least as durable as surface-treated material. If lenses are used, they must be molded from resin with maximum heat resistance and durability, or similar.

The combined LED modules, reflecting plates or lenses, and translucent covers must fully maintain their optical performance.

(iv)	Rubber Seals

Seals must be highly elastic and heat-resistant, must not absorb moisture, and must be resistance to deterioration.

(v)	Latches

If a latch design is used, to ensure the same quality as the original fixture, a chrome-plated JIS H 5301:2009 “Zinc Alloy Die-Cast” standard latch, synthetic resin baked finish JIS H 5302:2006 “Aluminum Allow Die-Cast” standard latch, or stainless (SUS304 or equivalent) JIS G 4305:2012 “Cold-Rolled Stainless-Steel Sheet and Steel Strip” standard latch must be used.

If a bracket bolt design is used, to ensure the same quality as the original fixture, electro-galvanized steel plate (standard size > 2.3 mm) hardware or SUS304 JIS G 4305:2012 “Cold-Rolled Stainless-Steel Sheet and Steel Strip” hardware or material with equivalent strength and durability greater than or equal to 2.0 mm in thickness must be used.

If a portion of the light body could be given a latch function, it must have equivalent strength. In addition, it must be designed to be strong enough not to easily spring open due to vibrations or earthquakes.

(vi)	Hinges and Hinge Axes

If a hinge design is used for the fixtures, a JIS G 4305:2012 “Cold-Rolled Stainless-Steel Sheet and Steel Strip” stainless (at least SUS304B or equivalent) hinge with a standard thickness of at least 1.5 mm must be used, and the hinge axis must be JIS G 4303:2012 “Stainless Steel Rod” stainless (at least SUS304B or equivalent).

Combined units of hinge and hinge axis may be used, but they must have straight equivalent to the above.

(vii)	Fixture Internal Wiring

Fixture internal wiring and external wiring shall be connected via a terminal block or waterproof connector.

Fixture internal wiring shall be connected to the terminal block by crimp terminals only.

(viii)	Terminal Blocks

If terminal blocks are used, the terminals must be porcelain, creepage distance must be at least 6mm, and air clearance must be at least 4mm. Labels of  , Ｅ,  or “earth” shall be included near the ground terminals.

(ix)	Pole Support Hardware

Pole support hardware shall be electro-galvanized steel plate or surface-treated JIS H 5302:2006 “Aluminum Alloy Die-Cast” ADC12 or other material (including coating if needed) with equivalent strength, anti-rust and anti-corrosion properties.

(x)	Coating

Rust-proofing treatment shall be applied to the main body, and then a top coat of at least one layer of synthetic resin-based paint shall be applied internally and externally. The coating must have equivalent strength, anti-rust and anti-corrosion properties as baked coating.

(e)	Performance

Optical performance of fixtures must be measured according to the method standardized in JIS C 8105-5:2014, and must satisfy the performance indices and recommended values stipulated in “Road Lighting Facilities Installation Standards/Explanations” (October 2007, Japan Road Association) chapters 3, 4, and 7.

(i)	Luminous Intensity Classification

Luminous intensity distribution shall use cut-off distribution as a standard, but may use semi-cut-off luminous intensity distribution if necessary due to installation conditions or the surrounding environment.

(ii)	Luminosity Value

The luminous intensity for fixtures mounted on a linear light pole with a rated luminous flux of about 10,000 lm at a horizontal angle of (ø) 90 degrees must satisfy the values shown in Table 52-9.

Table 52-9: Luminosity Value

| Luminous Intensity Type | Luminosity (cd/1,000 lm) |  |
| --- | --- | --- |
|  | Vertical Angle (θ) 90 degrees | Vertical Angle (θ) 80 degrees |
| Semi-Cut-Off Type | < 30 | < 120 |

(iii)	Utilization Factor

The utilization factor must satisfy the values shown in Table 52-10 below for fixtures mounted on a linear lighting pole.

Table 52-10: Utilization Factor

| Fixture Type | Area | Highway Width / Mounting Height |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | 0.5 | 1.0 | 1.5 | 2.0 |
| White LED Road Light Fixture | Road-Side | > 0.30 | > 0.51 | > 0.60 | > 0.61 |
|  | Sidewalk-Side | < 0.21 | < 0.29 | － | － |

(iv)	Upward Light Flux Ratio (Upper Hemisphere Light Flux Ratio)

The upward light flux ratio (upper hemisphere light flux ratio) must be less than 5% for fixtures mounted on a linear lighting pole.

(v)	Insulation Resistance

Must satisfy the capacities in (1) when measured according to the method standardized in JIS C 8105-1:2013.

When tested as detailed in (2), insulation resistance must be greater than or equal to 5 MΩ. Also, when tested in the cold, it must be greater than or equal to 30 MΩ.

For the insulation resistance test, lamps must be lit continuously until all parts of the fixture have reached roughly the same temperature. Then, the insulation resistance of both terminals and the non-charging metal parts must be measured with a 500 V Insulation Resistance Meter or other instrument with greater precision, as standardized in JIS C 1302:2014 “Insulation Resistance Meter.”

(vi)	Voltage Resistance

Must satisfy the capacities in (1) when measured according to the method standardized in JIS C 8105-1:2013.

Voltage resistance must withstand the voltage delivered when tested as detailed in (ii).

The voltage resistance test must be conducted directly after the insulation resistance test, sending a test voltage (2U+1000 V) close to a sign wave of 50 Hz or 60 Hz in frequency between the charged parts and non-charged parts for about one minute, and checking that no abnormalities occur.

If independent LED module controllers for installation outside the fixture are used, measurement shall include the combined fixture and controllers.

(vii)	Thermal Shock Resistance

The thermal shock resistance of fixtures must satisfy the following capacities at the time of testing using the JIS C JIS C 8105-2-3:2011 standard method.

When thermal shock resistance is tested according to (2), the fixture exterior and translucent cover must not crack, warp, or break.

For the thermal shock resistance test, the fixture should be illuminated as it would be for normal use, until all parts of the fixture have reached roughly the same temperature. At this point, water 10 °C colder than the surrounding temperature shall be poured on the translucent cover to simulate rain for the test. However, the simulated rainwater should be no colder than 4°C.

(viii)	Vibration Resistance

When the fixture is securely mounted and subject to a vibration test of increasing vibrations of between 500 and 800 times per minute, with a double amplitude of 2 - 3 mm, for a total of five minutes, the bolts on the mounting must not have loosened, and the fixture must not be broken.

(6)	LED MODULES FOR ROAD LIGHTING

Applicable Standards:

The following standards shall be applied to LED modules for road lighting, along with these specifications.

JIS C 8152-2:2014	White Lighting Luminous Diode (LED) Measurement Methods, Part 2:

LED modules and LED light engines

JIS C 8154:2009	General Lighting LED Modules – Safety Specifications

JIS C 8155:2010	General Lighting LED Modules – Required Performance

(a)	LED Module Performance

LED modules shall be contained within fixtures with a protection class rating high than IP44, as standardized in JIS C 8105-1：2013 “Lighting Components – Part 1: General Safety Requirement Rules,” and shall be designed for appropriate heat dissipation, to maintain the standard luminous flux continuously over the long term.

The initial characteristics of the combined module and module control device must satisfy Table 52-11, and satisfy also the requirements of LED Module Standard Luminous Flux for lighting equipment.

Table 52-11: LED Module Initial Characteristics (Full Illumination)

| Type | Initial Characteristics (Rated) |  |
| --- | --- | --- |
|  | Correlated Color Temperature (K) | Average Color Rendering Index Ra |
| White LED for Road Lighting | 4500 ±2000 | > 60 |

(b)	LED Module Lifespan

(i)	Lifespan

The total illumination time elapsed before the LED modules illuminated according to standard conditions cease to illuminate, or the total illumination time elapsed before their luminous flux falls below 80% of the value (LED module standard luminous flux) measured at initial illumination (regarded as non-lighting) shall be compared, and the shorter of the two-time spans shall be considered the lifespan of the LED modules.

(ii)	Rated Lifespan

The published average value for the time elapsed until the survival rate calculated based on the number of units which have ceased to function in a group of LED modules of the same type manufactured at the same time falls to 50% shall be considered the rated lifespan, and the value is shown in Table 52-12.

Table 52-12: LED Module Lifespan

| Type | Rated Lifespan (h) |
| --- | --- |
| White LED for Road Lighting | > 60,000 |

Alternatively, in addition to manufacturer testing, rated lifespan can be estimated logically based on the LED unit manufacturer’s LED operation conditions specifications for temperature and current, the technical data showing the change over time of the optical performance maintenance rate, the LED element temperature depending on the condition of the fixture, etc.

Regarding LED module rated lifespan, fixtures must be engineered for heat dissipation greater than or equal to the value shown in Table 52-12, and LED modules must be selected accordingly.

(iii)	Method for Calculating Lifespan

LED module lifespan testing must be conducted according to JIS C 8155:2010 Appendix C (Luminous Flux Maintenance Test and Lifespan Test Illumination Conditions).

The estimated lifespan of LED modules must be calculated using one of the methods below.

Value estimated using Illuminating Engineering Society of North America (IES) LM-80 (Luminous Flux Maintenance Rate Measurement Method) and TM-21 (Long-Term Luminous Flux Maintenance Rate Estimation Method)

Lifespan value estimated from the Arrhenius plot of temperature acceleration test results based on the use temperature

Lifespan estimation conditions shall be set as a fixture ambient temperature of 30 °C, with normal rated current flowing to the LED modules mounted in the fixture.

(7)		Led Module Control Units for Road Lighting

(a)	Applicable Standards

The following standards shall be applied to LED module controllers for road lighting, along with these specifications.

JIS C 8147-1:2011	Lamp Controllers - Part 1: General Rules and Safety Requirements

JIS C 8147-2-13:2014	Lamp Controllers - Part 2-13: Individual Requirements for LED Module Controllers for DC or AC Power Supply

JIS C 8153:2009	LED Module Controllers – Performance Requirements

JIS C 61000-3-2:2011	Electromagnetic Compatibility – Part 3-2: Limit Value – Harmonic Current Generation Limit Value

(Device with input current of less than 20A per phase)

JIS C 61000-4-5:2009	Electromagnetic Compatibility - Part 4-5: Testing and Measuring Technology – Surge Immunity Testing

(b)	LED Module Control Device Performance

(i)	Design and Materials

Design and materials are stipulated in JIS C 8147-2-13:2014.

(ii)	Dimensions

If the devices are stored within the light poles, each part must be arrayed as in the figure shown here after, must fit within the reference dimensions shown in Table 52-13, must be easily mounted or taken out with the joint box.

Table 52-14 shows reference dimensions for pole internal diameter and LED module controllers which can be stored on the diagonal for LED Module control device mounting in a lighting taper pole.

If LED module controllers are housed within fixtures, their geometry and mass must satisfy the standards shown in in Sub-Clause (5)(c)(i) of this Sub-Section.

Dimensions of LED Module Controllers to be Stored in Light Poles

Table 52-13: LED Module Control Device Dimensions

| Length A (mm） | Width B (mm) | Height C (mm） | Application |
| --- | --- | --- | --- |
| <550 | <125 | <120 | Stored in pole |

Note 1: If more than one LED module controllers are used, sufficient consideration must be taken for whether they will fit inside the pole.

Table 52-14: Lighting Taper Pole LED Module Control Device Mounting Location Internal Diameter Dimensions

| Pole Height (m) | Pole Type | LED Module Control Device Mounting Hook Position Internal Diameter D (mm) | Diagonal Dimensions for Internally Storable LED Module Controllers (mm) |
| --- | --- | --- | --- |
| 10 | Liner Type ; For 1 Lamp | 152 | 147 |

(iii)	Lead Wires

Lead wires must demonstrate performance equivalent to JIS C 3306:2000 “Vinyl Cord” or JIS C 3327:2000 “600V Rubber Cabtyre Cable,” with a nominal cross-sectional area of at least 0.75 mm2.

If insulated wires are used, wires with performance equivalent to JIS C 3307:2000 “600V Vinyl Insulated Wire (IV)” must be used for housing within poles, and JIS C 3317:2000 “Grade heat-resistant polyvinyl chloride insulated wires” must be used for housing within fixtures, and the nominal cross-sectional area must be at least 0.75 mm2.

For housing within poles, lead wires must be at least 700 mm in length.

(iv)	Performance

LED Module controllers must have sufficient power supply capacity for the LED modules in their light fixture.

If LED module controllers are housed within poles, they must bear up over the long term to power being switched on or off once per day in response to temperature and humidity conditions inside the pole. If LED module controllers are housed within fixtures, the fixtures must have a protection class rating of at least IP44, as standardized in JIS C 8105-1:2013 “Lighting Components – Part 1: General Safety Requirement Rules,” so as to bear up over the long term to power being switched on or off once per day in response to temperature and humidity conditions inside the pole.

(v)	Characteristics of Road Lighting LED Module Controllers

Rated input voltage of road lighting LED module controllers shall be AC200. The main characteristics of road lighting LED module controllers are shown in Table 52-15.

Table 52-15: Characteristics of Road Lighting LED Module Controllers

| Fixture Type | Rated Input Voltage (V) | Rated Input Current (A) | Rated Electricity Consumption (W) | Power Factor （％） |
| --- | --- | --- | --- | --- |
| White LED Road Lighting Fixtures | 415 | <0.70 | <120 | >85 |

Note 2: If the rated input voltage exceeds 240 V, it can be combined with the transformer.

(vi)	Humidity Resistance and Insulation

LED module controllers housed within light poles must satisfy the performance below when measured according to the method standardized in JIS C 8147-1:2011.

Controllers must be kept in continuously humidified container with relative humidity of 91% - 95% for over 48 hours, and directly after humidifying, about 500 V of DC voltage must be applied for one minute, and the insulation resistance measured must be greater than or equal to 2 MΩ.

(vii)	Noise Characteristics

Noise terminal voltage from the light fixtures and noise power from the light fixtures must satisfy the performance listed below when measured by the method stipulated in the Electrical Appliances and Materials Safety Act.

If independent LED module controllers for installation outside the fixture are used, measurement shall include the combined fixture and controllers.

Terminal Voltage	526.5 kHz - 5 MHz: < 56 dB

- 5 MHz - 30 MHz: < 60 dB

Noise Power	30 MHz - 300 MHz: < 55 dB

(viii)	Harmonic Current

Relative limit values for fixtures whose active input power exceeds 25 W (Class C: lighting devices) shall be less than those standardized in JIS C 61000-3-2:2011.

If independent LED module controllers for installation outside the fixture are used, measurement shall include the combined fixture and controllers.

Table 52-16: Relative Limit Values for Class C Devices

| Harmonic Degree n |  | Maximum Permissible Harmonic Currents as a Percentage of Light Fixture Fundamental Harmonic Input Current (%) |
| --- | --- | --- |
| Even Harmonics | 2 | 2 |
| Odd Harmonics | 3 | 30×λ Note) |
|  | 5 | 10 |
|  | 7 | 7 |
|  | 9 | 5 |
|  | 11≦n≦39 | 3 |

Note: λ indicates circuit power factor

(ix)	Surge Protection

Surge protection must be greater than or equal to that necessary for voltage loads of 15 kV for common mode (ground) and 2 kV for normal mode (wire), as standardized for class X conditions in JIS C 61000-4-5:2009.

If independent LED module controllers for installation outside the fixture are used, measurement shall include the combined fixture and controllers.

(x)	Initial Luminous Flux Correction

A function must be included which automatically adjusts excess brightness at the time of installation to a standard brightness level (at least 80% of the rated luminous flux value). The initial luminous flux correction method shall be automatic, using light sensors to measure the interior brightness of the light fixtures, or using program control.

(c)	LED Module Control Device Lifespan

(i)	Lifespan

The total illumination time elapsed before the LED module controllers operating under standard conditions either break, or their output falls below the rated value and they become unusable, shall be considered the lifespan of the LED module controllers.

(ii)	Rated Lifespan

The average value for the time elapsed until the lifespan survival rate of a group of LED module controllers of the same type manufactured at the same time falls to 50% shall be considered the rated lifespan, and the value is shown in Table 52-17.

Table 52-17: LED Module Control Device Rated Lifespan

| Type | Rated Life Span（h） |
| --- | --- |
| White LED for Road Lighting | > 60,000 |

Circuits must be designed and parts selected such that components housed within fixtures or light poles for use may operate for longer than their rated lifespan.

(iii)	Lifespan Calculation Method

The manufacturer shall report to the client on the basis for the engineered lifespan of the LED module controllers, achieved using one of the methods below.

Regarding the ambient temperature and installation conditions for estimating lifespan, if the LED module control device is housed within the fixture, the estimate shall use a fixture ambient temperature of 30 ℃ when mounted, and if the decide is installed within the pole, the estimate shall use an ambient temperature of 40 ℃, with the rated current being supplied to the LED modules.

Lifespan value estimated from the Arrhenius plot of temperature acceleration test results based on the use temperature

Lifespan value estimated based on calculations using the maximum temperature derating factor, etc. for the main components used

Value calculated using lifespan value estimated via a method standardized by the LED module control device manufacturer and ambient temperature conditions during actual installation

(8)	Inspections

LED roadway light fixtures (fixtures, LED modules, LED module controllers) shall be subject to the inspections of the following points.

(a)	In-House Inspection

- Lighting Characteristics

- LED Module Controller Apparent Power

- Design

- Light Characteristics (cutoff light distribution, upward light flux ratio, lighting utilization factor)

- Insulation Characteristics

- Voltage Resistance

- Thermal Shock Resistance

- Vibration Resistance

- LED Module Capacity

- LED Module Lifespan

- Characteristics

- Humidity Resistance and Insulation

- Noise Characteristics

- Harmonic Current

- Lightning Surge Resistance

- Initial Luminous Flux Correction Function

- LED Module Controller Lifespan

(b)	On-Site Inspection

- Luminosity shall be measured

5300.	EMERGENCY FACILITIES

(1)	Description

(a)	Emergency Facility Design

The emergency facilities are composed of the devices below.

Tunnel Entrance Warning Signs (DL Board)

Internal Tunnel Warning Signs (EL Board)

Monitoring Control Panel

Monitor Panel

Emergency Telephone

Digital Electronic Switchboard (PBX)

Evacuation Guidance Display/Display Lights

(b)	Applicable Standards

Unless otherwise specified, items in this list of specifications shall apply the following standards.

International Electrotechnical Commission (IEC) Recommended Standard

International Telecommunication Union-Telecommunication Standardization Sector Recommendations (ITU-T)

International Standards (ISO)

Japanese Industrial Standards (JIS)

VCCI Association’s Independent Standard Measures Operation Standards

International Commission on Illumination (CIE) Standards

Other related laws

(2)	Tunnel Entrance Warning Signs (Dl Board)

(a)	Applicable Standards

Applicable Standards

Facility Guidelines No. 8 Telecommunication Facilities. (NEXCO RI July 2017)

Facility Material Specifications Manual Electricity Variable Road Information Board Facilities. (NEXCO RI July 2017)

Facility Material Specifications Manual Electricity Evacuation Guidance Facility Standard Specifications Manual. (NEXCO RI July 2012)

Electronic Telecommunications Facilities Design Guidelines/Explanation (Electric Version) 2017 Edition. The Telecommunications Association

Electronic Telecommunications Facilities Installation Standard Diagrams January 2015. The Telecommunications Association

(b)	Device Specifications

These facilities shall be composed of the following elements.

Transmission Control Device

Display Unit

Name Unit

Warning Unit

Flashing Lamps

Housing Unit

Power Supply

(c)	Structure

The dimensions of the housing shall be at least 3540mm wide x at least 1950mm high × at least 1080mm deep. However, these dimensions exclude protruding elements.

The weight of the housing must be less than 2000kg.

The housing material must be of higher specification than SPCC (JIS G 3141) 2.3t or equivalent.

The exterior of the housing must be pretreated with blast treatment followed by zinc spraying (JIS H 8300 TS-WF or TS-ES/Zn99.99(50)), and the interior must also be coated with a coating equivalent or better than primer, intermediate coating, and external coating with two layers of polyurethane resin.

The waterproofing and dust-proofing of the housing must rank above IP43 protection class, as standardized in JIS C 0920 “protection classes (IP codes) for the exterior of electronic devices.”

The top and back sides of the housing must include heat shielding plates, which must be made of a material high rated than aluminum alloy (JIS H 4000 A5052P) 2.0t or equivalent.

Maintenance and inspections must be able to be conducted from the inside of the housing. Entry/exit doors must be designed with consideration for the work environment and for safety, and must be positioned in a location which makes inspection easy.

Electrical noise must meet the VCCI Class A technological standard.

The entry/exit doors to the housing must include a handle with a lock.

The side of the housing must include air circulation windows which can be opened and shut.

The interior of the housing must include lighting which can be used during maintenance and inspections.

The housing must include a testing-in-progress sign. The sign must be designed so that it will only display when needed.

(d)	Display

The display shall be made up of display units, and each unit within the information board must be compatible with all other units. In addition, each display unit must be individually replaceable within the housing.

The waterproofing of the display must rank above IPX5 protection class, as standardized in JIS C 0920 “protection classes (IP codes) for the exterior of electronic devices.”

The display must be viewable by the drivers of moving cars, and must be angled three degrees forward with respect to the housing.

The color of the display panel background must be equivalent to black (Munsell N1.5 without gloss).

The display panel must be designed to prevent loss of visibility due to direct sunlight from above the lighting elements.

The display panel must be designed to prevent loss of visibility due to rain droplets.

(e)	Main Performance

(i)	Display Color and Display Chromaticity

Display chromaticity must match the chromaticity coordinate points shown in Table 53-1 in the JIS Z 8110 “Colour Specification - Names of Light-source Colour” reference diagram 1, “General Chromaticity Distinctions for System Color Names.”

However, measurement conditions must match JIS Z 8703 “Test Location Standard Conditions,” and the measurement method must follow JIS Z 8724 “Methods of Colour Measurement-Light-Source Colour”.

Furthermore, the dominant wavelengths must be determined based on the intersection point between the spectrum locus and the line extension tying together the white point (x=0.333, y=0.333) and the display color chromaticity coordinates as specified in JIS Z 8701 “Colour Specification” / The CIE 1931 Standard Colorimetric System and the CIE 1964 Supplementary Standard Colorimetric System; Appendix: “Chromaticity Display Methods Based on Main Wavelengths (or Complementary Wavelengths) and Excitation Purity,” Table 53-1, “Dominant Wavelength.”

Table 53-1: Display Color Chromaticity Coordinates and Dominant Wavelength

| Display Color | Chromaticity Coordinates |  | Dominant Wavelength |
| --- | --- | --- | --- |
|  | x | y |  |
| Red | 0.697 | 0.303 | 623nm |
| Orange | 0.614 | 0.385 | 597nm |
| Yellow | 0.430 | 0.500 | 572nm |
| Yellow-Green | 0.320 | 0.590 | 552nm |
| Green | 0.210 | 0.490 | 510nm |
| White | 0.290 | 0.300 | 481nm |
| Cyan | 0.170 | 0.250 | 485nm |

(ii)	Display Unit Brightness

Measurement conditions must meet JIS Z 8703 “Standard Atmospheric Conditions for Testing”.

Daytime Display

The brightness for each display color during daylight is stipulated in Table 53-2 below.

Table 53-2: Daytime Display Brightness

| Display Color | Brightness |
| --- | --- |
| Red | Standard 1600cd/m2 |
| Orange | Standard 2900cd/m2 |
| Yellow | Standard 3800cd/m2 |
| Yellow-Green | Standard 2200cd/m2 |
| Green | Standard 2200cd/m2 |
| White | Standard 4300cd/m2 |
| Cyan | Standard 2700cd/m2 |

Nighttime Display

The brightness for each display color during nighttime is stipulated in Table 53-3 below.

Table 53-3: Nighttime Display Brightness

| Display Color | Brightness |
| --- | --- |
| Red | Standard 85cd/m2 |
| Orange | Standard 205cd/m2 |
| Yellow | Standard 205cd/m2 |
| Yellow-Green | Standard 120cd/m2 |
| Green | Standard 120cd/m2 |
| White | Standard 230cd/m2 |
| Cyan | Standard 145cd/m2 |

Display Response Time

The time between receipt of the display control signal from the monitoring control panel and the illumination of the display must be less than three seconds.

(f)	Functions and Specifications

(i)	Functions

Display Control Functions

The transmission control must control the display, flashing, etc. in accordance with the display control signal from the monitoring control panel, and send a status monitoring signal from the information boards to the monitoring control panel.

In addition, the illumination of the name unit shall be controlled by transmission control element in accordance with the switch between day and night displays.

Character Array Equalization Function

Character array equalization and centering must take place automatically according to the number of characters.

Control Information Holding Function

Display control signal data content will be held until a new display signal is received from the monitoring control panel.

Lighting Time Equalization Function

Display characters must move at least 30mm vertically and horizontally, and display element lighting time must be equalized.

However, this does not include symbol displays.

Display character movement time interval: every 15 minutes ±10%

Movement time switch time: less than 500μs

Display Character Holding Function

If two lighting elements in the character display malfunction at once, the character must be automatically displayed to avoid the malfunctioning units, regardless of the character array equalization function. Display units shall be arrayed in vertical lines of 16 × horizontal lines of 16, and breakdown detection units must match this.

If the character cannot be displayed to avoid the malfunctioning display units, character display will continue with the malfunctioning unit block switched off.

Off-Switch Control Function

If the display light source electric power value exceeds the standards, shutoff control shall take place automatically. In addition, lighting must be restorable through remote control.

Breakdown Output Function

When the following situations occur, a breakdown signal shall be sent as output to the monitoring control panel:

- If a display unit malfunctions

- If the display light source electric power value exceeds the respective value herein specified for Power Consumption.

Blackout-Response Functions

In response to a blackout of less than 250ms, the transmission control unit shall operate as it would at times of normal power.

Brightness Adjustment Function

- To prevent loss of visibility during daytime display, display brightness must adjust automatically according to changes in the lighting conditions in front of the display.

- The difference in lighting between daytime display and nighttime display shall be 200Lx, and chattering at lighting conditions near this cutoff value shall be prevented.

- Display brightness shall be manually adjustable in response to dirtying or deterioration of the display elements.

(ii)	Transmission Control Functions

Display control signals, monitoring control signals, edit control signals, test control signals, and status monitoring signals shall be received and transmitted.

In response to a monitoring request from the monitoring control panel, an output of status monitoring items listed in Table 53-4 shall be sent.

Table 53-4: Status Monitoring Items

| Item | Content |
| --- | --- |
| Test | Under test control from the monitoring control panel |
| Breakdown | Power supply breakdown, unit breakdown and board breakdown |
| Manual | Information board (controller unit) is set to test mode (manual operation) |
| Congestion | Transmission error such as unregistered signal and control processing error, etc. |

Test Control Functions

Between the time when the transmission control unit receives the “test start” signal from the monitoring control panel and the time it receives the “test stop” signal, no display items will be displayed even if a display control signal is received, allowing for tests to be conducted on display control functions.

However, if the display is illuminated, the display board illumination should be shut off.

After the transmission control unit receives the “test start” or “test stop” signal from the monitoring control panel, information board status monitoring items will be sent to the monitoring control panel.

(iii)	Device Specifications

Display

- Display character height shall be standardized at 450mm.

- The number of possible symbol patterns which can be registered must exceed 30.

Surge Protection

Measures must be taken to ensure that surge protection satisfies the JIS C 5381-21 “Functions and Test Methods for Surge Protection Devices Connected to Transmission and Signal Circuits” category C2 standard.

Display

- Functions

① Lamp Functions

② Brightness Switch

③ Ensure Display Uniformity

④ Brightness at the Angle of Radiation

- Display Functions

The display shall display characters and symbols as follows:

① 7 characters (Japanese) equivalent ×2 line display

② Symbol＋5 characters (Japanese) equivalent ×2 line display

However, symbols will be displayed at the left edge of the display board.

- Display Specifications

① Display Unit

    - Display Elements: LED

    - Design: RGB collected method or combined method

    - Center Brightness: >5000cd/m2 (white: red, green, and blue simultaneous illumination)

    - Display unit dimensions shall be less than 160mm in width × less than 160mm in height.

② Display Board

    - Display dot array: at least 108 vertical rows × at least 336 horizontal rows (excluding blank area)

- (Symbol display area: at least 108 vertical rows × at least 96 horizontal rows)

    - Display dot pitch:	10mm equivalent pitch

The blank area shall be located between the upper and low character rows, excluding symbol display areas, and must be at least 120mm in height.

(iv)	Name Unit Functions

Functions

- Illumination Functions: The name unit shall be illuminated or shut off in response to a display control signal sent from the transmission control unit.

- White Area Average Brightness: The initial value for white area average brightness in the display board shall be at least 260cd/m2. However, the uniform brightness (maximum value/minimum value) for the same color shall be less than 4.

- Illumination Format: Illumination shall be provided by LEDs.

Specifications

- Display Format: Internal illumination format

- Character Color: Display will be white characters on a green background.

- Display Board: Display unit dimensions shall be 2000mm in width × about 400mm in height, and must be made of a material with greater strength and weather resistance then methacrylic resin board (JIS K 6718-2) 8t or equivalent material.

(v)	Warning Device Functions

Alarm Sounding Function: A siren shall sound or cease sounding in response to a display control signal from the transmission control unit.

Specifications:

- The speakers shall be outdoor-typehorn speakers (JIS C 5504).

- The siren volume must fall between 90 phon and 120 phon at a distance of 20m from the speaker.

- Siren sound shall be a repeated electronically generated compound wave.

- The length of time for which the siren sounds shall be set between zero and ten minutes.

(vi)	Flashing Function

Illumination: A display control signal from the transmission control unit shall interlock with the illumination of the display to control illumination or shutoff of one yellow flashing lamp or two red flashing lamps, and adjust the flashing between two levels of brightness. When red lamps are illuminated, they must be lit alternately.

Daytime Display:

- Red Lamp: > standard 7000 cd/m2

- Yellow Lamp: > standard 7000 cd/m2

Nighttime Display:

- Red Lamp: standard 1800 cd/ m2

- Yellow Lamp: standard 1800 cd/ m2

Specifications

- Display Elements

- Display Element LEDs

- Chromaticity

    - Red Lamps: Shall be in accordance with CIE S 004/E-2001 “Colors of Light Signals,” “Table 2 - Coordinates of Intersection Points of Allowed Chromaticity Area Boundaries,” “Red Light Signal Colors Class A1.”

    - Yellow Lamps: Shall be in accordance with CIE S 004/E-2001 “Colors of Light Signals,” “Table 2 - Coordinates of Intersection Points of Allowed Chromaticity Area Boundaries,” “Yellow Light Signal Colors.”

(vii)	Lifespan

Flashing LED lifespan shall be measured under the temperature and humidity conditions in “JEITA ED-4701/100 [Semiconductor Device Environment and Durability Testing Methods (Lifespan Test I) Test Method 102 High-Temperature High-Humidity Bias Test Table 1 High-Temperature High-Humidity Preservation Test Conditions Test Conditions Code B],” and shall be considered the time elapsed until initial brightness falls by half, which must be at least 4000 hours.

(g)	Interface

The conditions for the interface between the DL information board and the monitoring control panel are shown below:

- SHDSL Modem

LAN-Side Interface

Applicable Standards: 	10BASE-T, 100BASE-TX

Transmission Method	IEEE802.3 / IEEE802.3u

Transmission Speed	10 / 100Mbps

No. of Ports	4 ports

Applicable Connector	RJ-45 connector

(ii)	SHDSL-Side Interface

Applicable Standards	ITU-T G.991.2

Transmission Speed	512kbps - 5.6Mbps

Transmission Distance:

- 10.2km (512kbps, 0.65mm, 2 wire time, theoretical value)

- 3.4km (5.6Mbps, 0.65mm, 2 wire time, theoretical value)

No. of Ports	At least 2 ports

Applicable Line	Independently operated metal line (2W)

Applicable Connector	RJ-11

(h)	Operation Conditions

Conditions under which these facilities can be operated normally are shown in Table 53-5.

Table 53-5: Classification of Operation Conditions

Operation Conditions

IEC60721-3-4 Environmental Conditions 4K2/4Z5/4Z7/4B1/4C2/4S3/4M4 K: Weather Conditions Z: Special Weather Conditions B: Wildlife Conditions C: Chemically Active Substances S: Mechanically Active Substances M: Mechanical Conditions

However, the lower temperature of the air surrounding the facility shall be -20°C.

For details, refer to IEC 60721-3-4 “JIS C 60721-3-4 [Classification of Groups of Environmental Parameters and their Severities]”.

(i)	Power Supply

(i)	Input Conditions

Standard input voltage for these facilities is shown below.

AC three-phase three-wire 415V±10% (50Hz)

(ii)	Power Consumption

Power consumption for these facilities must be less than 1200VA.

However, power consumed shall be capacity at 35% of full (daytime white) illumination, and exclude maintenance power.

(j)	Insulation Resistance

Insulation resistance must be at least 10MΩ, and must be measured with a DC 500 V Insulation Resistance Meter. (Surge protection devices shall be excluded). Measurement locations are shown in Table 53-6.

Table 53-6: Insulation Resistance Measurement Location and Measurement Conditions

| Measurement Location | Measurement Conditions |
| --- | --- |
| Between power supply terminal and grounding terminal | With earth removed |
| Between both transmission terminals | With external lines cut off |
| Between one transmission terminal and grounding terminal | With earth removed |

(k)	Voltage Resistance

Voltage resistance must result in no anomalies when AC 1500V is applied for one minute when input voltage is less than 250V, and AC 2000V is applied for one minute when input voltage is more than 250V. (Surge protection devices shall be excluded). Measurement locations are shown in Table 53-7.

Table 53-7: Voltage Resistance Measurement Location and Measurement Conditions

| Measurement Location | Measurement Conditions |
| --- | --- |
| Between power supply input and housing | With control system and earth removed |

(l)	Surge Protection

Surge protection shall be as stipulated in JIS C 5381-1 “Surge Protection Devices Connected to Low-Voltage Systems: Characteristics and Test Methods,” Class II.

(m)	Spare Items

Spare items for the facilities are shown in Table 53-8.

Table 53-8: Spare Items

| No | Part Name | Quantity |
| --- | --- | --- |
| 1 | Fuses | 100% |

(3)	Tunnel Entrance Warning Signs (EL) Board

(a)	Device Specifications

These facilities shall be composed of the following elements:

Transmission Control Unit

Display Unit

Flashing Lamps

Housing: The transmission control unit shall be housed within the display unit, and must include flashing lamps and a testing-in-progress sign

Power Supply Unit: Shall be mounted on the housing, shall bring in an external power supply, and shall supply the electricity needed to power each component of the information board

(b)	Structure

(i)	Housing dimensions shall be less than 2400mm wide × less than 800mm tall × less than 500mm deep. However, this excludes protruding elements.

(ii)	The housing shall weigh less than 550kg.

(iii)	The housing shall be made of an equivalent or better material then SPCC (JIS G 3141) 2.3t.

(iv)	The exterior of the housing must be pretreated with blast treatment followed by zinc spraying (JIS H 8300 TS-WF or TS-ES/Zn99.99(50)), and the interior must also be coated with a coating equivalent or better than primer, intermediate coating, and external coating with two layers of polyurethane resin.

(v)	The waterproofing and dust-proofing of the housing must rank above IP54 protection class, as standardized in JIS C 0920 “protection classes (IP codes) for the exterior of electronic devices.”

(vi)	Maintenance and inspections must be able to be conducted from the back side of the housing.

(vii)	Electrical noise must meet the VCCI Class A technological standard.

(viii)	The maintenance doors of the housing must not be easily opened and closed by a third party.

(ix) 	The interior of the housing must include lighting which can be used during maintenance and inspections.

(x)	The housing must include a testing-in-progress sign. The sign must be designed so that it will only display when needed. The testing-in-process sign must have superior durability, and the mounting must be mechanically strong.

(c)	Display

(i) 	The display shall be made up of display units, and each unit within the information board must be compatible with all other units. In addition, each display unit must be individually replaceable from the back of the housing.

(ii) 	The waterproofing of the display must rank above IPX5 protection class, as standardized in JIS C 0920 “protection classes (IP codes) for the exterior of electronic devices.”

(iii) 	The color of the display panel background must be equivalent to black (Munsell N1.5 without gloss).

(iv) 	The display panel must include tempered glass (JIS R 3206) 8t to protect against air and water pressure from cleaning, etc.

(d)	Main Performance

(i)	Display Color and Display Chromaticity

Display chromaticity must match the chromaticity coordinate points shown in Table 9 in the JIS Z 8110 “Color Display Methods – Light Source Color Names” reference diagram 1, “General Chromaticity Distinctions for System Color Names.”

However, measurement conditions must match JIS Z 8703 “Test Location Standard Conditions,” and the measurement method must follow JIS Z 8724 “Color Display Methods – Light Source Colors.”

Furthermore, the dominant wavelengths must be determined based on the intersection point between the spectrum locus and the line extension tying together the white point (x=0.333, y=0.333) and the display color chromaticity coordinates as specified in JIS Z 8701 “Colour Specification” / The CIE 1931 Standard Colorimetric System and the CIE 1964 Supplementary Standard Colorimetric System; Appendix: “Chromaticity Display Methods Based on Main Wavelengths (or Complementary Wavelengths) and Excitation Purity,” Table 53-9, “Dominant Wavelength.”

Table 53-9: Display Color Chromaticity Coordinates and Dominant Wavelength

| Display Color | Chromaticity Coordinates |  | Dominant Wavelength |
| --- | --- | --- | --- |
|  | x | y |  |
| Red | 0.697 | 0.303 | 623nm |
| Orange | 0.614 | 0.385 | 597nm |
| Yellow | 0.430 | 0.500 | 572nm |
| Yellow-Green | 0.320 | 0.590 | 552nm |
| Green | 0.210 | 0.490 | 510nm |
| White | 0.290 | 0.300 | 481nm |
| Cyan | 0.170 | 0.250 | 485nm |

(ii)	Display Unit Brightness

Measurement conditions must meet JIS Z 8703 “Test Location Standard Conditions.”

Tunnel Internal Display

The brightness of each color in the tunnel internal display is shown in Table 53-10.

Table 53-10: Tunnel Internal Display Brightness

| Display Color | Brightness |
| --- | --- |
| Red | Standard 85cd/m2 |
| Orange | Standard 205cd/m2 |
| Yellow | Standard 205cd/m2 |
| Yellow-Green | Standard 120cd/m2 |
| Green | Standard 120cd/m2 |
| White | Standard 230cd/m2 |
| Cyan | Standard 145cd/m2 |

Display Response Time

The time between receipt of the display control signal from the monitoring control panel and the illumination of the display must be less than three seconds.

(e)	Functions and Specifications

(i)	Functions

Display Control Functions: The transmission control unit must control the display, flashing, etc. in accordance with the display control signal from the monitoring control panel, and send a status monitoring signal from the information board to the monitoring control panel.

Character Array Equalization Function: Character array equalization and centering must take place automatically according to the number of characters.

Control Information Holding Function: Display control signal data content will be held until a new display signal is received from the monitoring control panel.

- Lighting Time Equalization Function:

- Display characters must move at least 30mm vertically and horizontally, and display element lighting time must be equalized.

- Display character movement time interval: every 15 minutes ±10%

- Movement time switch time: less than 500μs

Display Character Holding Function: If a lighting element in the character display malfunctions, the character must continue to be displayed with the malfunctioning unit switched off. Display units shall be arrayed in vertical lines of 16 × horizontal lines of 16, and breakdown detection units must match this.

Off-Switch Control Function: If the display light source electric power value exceeds the respective value herein specified for Power Consumption, shutoff control shall take place automatically. In addition, lighting must be restorable through remote control.

Breakdown Output Function: When the following situations occur, a breakdown signal shall be sent as output to the monitoring control panel.

- If a display unit malfunctions

- If the display light source electric power value exceeds the respective value herein specified for Power Consumption

Blackout-Response Functions: In response to a blackout of less than 250ms, the transmission control unit shall operate as it would at times of normal power.

Brightness Adjustment Function: Display brightness shall be manually adjustable in response to dirtying or deterioration of the display elements.

(ii)	Transmission Control Functions

Display control signals, monitoring control signals, edit control signals, test control signals, and status monitoring signals shall be received and transmitted. In response to a monitoring request from the monitoring control panel, an output of status monitoring items listed in Table 53-11 shall be sent.

Table 53-11: Status Monitoring Items

| Item | Content |
| --- | --- |
| Test | Under test control from the monitoring control panel |
| Breakdown | Power supply breakdown, unit breakdown and board breakdown |
| Manual | Information board (controller unit) is set to test mode (manual operation) |
| Traffic Jam | Transmission error such as unregistered signal and control processing error, etc. |

Test Control Function

Between the time when the transmission control unit receives the “test start” signal from the monitoring control panel and the time it receives the “test stop” signal, no display items will be displayed even if a display control signal is received, allowing for tests to be conducted on display control functions.

However, if the display is illuminated, the display board illumination should be shut off.

After the transmission control unit receives the “test start” or “test stop” signal from the monitoring control panel, information board status monitoring items will be sent to the monitoring control panel.

(iii)	Device Specifications

Display

- Display character height shall be standardized at 450mm.

- Surge Protection

Measures must be taken to ensure that surge protection satisfies the JIS C 5381-21 “Functions and Test Methods for Surge Protection Devices Connected to Transmission and Signal Circuits” category C2 standard.

Display

- Functions

- ① Lamp Functions

- ② Ensure Display Uniformity

The display must appear uniform when viewed from any direction, front, left, right, above, or below.

However, the uniform brightness (maximum value/minimum value) for the same color shall be less than 1.37.

Brightness at the Angle of Radiation

The display unit must display brightness of at least 1825cd/m2 (daytime white) at ±10 degrees horizontal and vertical.

(iv)	Display Functions

Display: Must be able to provide the following character display or dot-free display. Width 5 characters (Japanese) equivalent Nepalese characters

Specifications:

- Display Unit

- Display Elements: LED

- Design: RGB collected method or combined method

- Center Brightness: > 5000cd/m2 (white: red, green, and blue simultaneous illumination)

- Display unit dimensions shall be less than 160mm in width × less than 160mm in height.

- Display unit lifespan shall be measured under the temperature and humidity conditions in “JEITA ED-4701/100 [Semiconductor Device Environment and Durability Testing Methods (Lifespan Test I) Test Method 102 High-Temperature High-Humidity Bias Test Table 1 High-Temperature High-Humidity Preservation Test Conditions Test Conditions Code B].” A 6000-hour acceleration test shall be conducted, and after 6000 hours have passed, the remaining brightness value after 10000 hours have passed shall be predicted based on the 6000-hour remaining brightness value and curve showing changes in brightness. This predicted value must be at least 50% of initial brightness. Alternatively, the remaining brightness value after a 10000-hour acceleration test must be at least 50% of initial brightness.

Display Board

- Display dot array: more than 45 vertical rows × more than 240 horizontal rows

- Display dot pitch: 10mm equivalent pitch

(v)	Flashing Lamps

Functions

- Illumination Functions: A display control signal from the transmission control unit shall interlock with the illumination of the display to control illumination or shutoff of one yellow flashing lamp or one red flashing lamp.

- Internal Tunnel Display

  - Read Lamp	standard 1800 cd/m2

  - Yellow Lamp: standard 1800 cd/m2

Specifications

- Display Elements

- Display Element LEDs

- Chromaticity

  - Red Lamps: Shall be in accordance with CIE S 004/E-2001 “Colors of Light Signals,” “Table 2 - Coordinates of Intersection Points of Allowed Chromaticity Area Boundaries,” “Red Light Signal Colors Class A1.”

  - Yellow Lamps: Shall be in accordance with CIE S 004/E-2001 “Colors of Light Signals,” “Table 2 - Coordinates of Intersection Points of Allowed Chromaticity Area Boundaries,” “Yellow Light Signal Colors.”

Lifespan: Flashing LED lifespan shall be measured under the temperature and humidity conditions in “JEITA ED-4701/100 [Semiconductor Device Environment and Durability Testing Methods (Lifespan Test I) Test Method 102 High-Temperature High-Humidity Bias Test Table 1 High-Temperature High-Humidity Preservation Test Conditions Test Conditions Code B],” and shall be considered the time elapsed until initial brightness falls by half, which must be at least 4000 hours.

(f)	Interface

The conditions for the interface between the EL information board and the monitoring control panel are shown below.

SHDSL Modem

- LAN-Side Interface

- Applicable Standards	10BASE-T, 100BASE-TX

- Transmission Method	IEEE802.3/IEEE802.3u

- Transmission Speed	10/100Mbps

- No. of Ports	4 ports

- Applicable Connector	RJ-45 connector

SHDSL-Side Interface

- Applicable Standards	ITU-T G.991.2

- Transmission Speed	512kbps-5.6Mbps

- Transmission Distance	10.2km (512kbps, 0.65mm, 2 wire time, theoretical value); and 3.4km (5.6Mbps、0.65mm, 2 wire time, theoretical value)

- No. of Ports	At least 2 ports

- Applicable Line	Independently operated metal line (2W)

- Applicable Connector	RJ-11

(g)	Operation Conditions

Conditions under which these facilities can be operated normally are shown in Table 53-12.

Table 53-12: Classification of Operation Conditions

Operation Conditions

IEC60721-3-4 Environmental Conditions 4K2/4Z1/4Z4/4Z8/4B1/4C2/4S3/4M4 K: Weather Conditions Z: Special Weather Conditions B: Wildlife Conditions C: Chemically Active Substances S: Mechanically Active Substances M: Mechanical Conditions

For details, refer to IEC 60721-3-4 “JIS C 60721-3-4 [Classification of Groups of Environmental Parameters and their Severities]”.

(h)	Power Supply

(i)	Input Conditions

Standard input voltage for the facilities is shown below:

AC three-phase three-wire 415V±10% (50Hz)

(ii)	Power Consumption

Power consumption for these facilities must be less than 400VA.

However, power consumed shall be capacity at 35% of full (white) illumination, and exclude maintenance power.

(i)	Insulation Resistance

Insulation resistance must be greater than 10MΩ, and must be measured with a DC 500 V Insulation Resistance Meter. (Surge protection devices shall be excluded). Measurement locations are shown in Table 53-13.

Table 53-13: Insulation Resistance Measurement Locations and Measurement Conditions

| Measurement Locations | Measurement Conditions |
| --- | --- |
| Between power supply terminal and grounding terminal | With earth removed |
| Between both transmission terminals | With external lines cut off |
| Between one transmission terminal and grounding terminal | With earth removed |

(j)	Voltage Resistance

Voltage resistance must result in no anomalies when AC 1500V is applied for one minute when input voltage is less than 250V, and AC 2000V is applied for one minute when input voltage is more than 250V. (Surge protection devices shall be excluded). Measurement locations are shown in Table 53-14.

Table 53-14: Voltage Resistance Measurement Locations and Measurement Conditions

| Measurement Location | Measurement Conditions |
| --- | --- |
| Between power supply input and housing | With control system and earth removed |

(k)		Surge Protection

Surge protection shall be as stipulated in JIS C 5381-1 “Surge Protection Devices Connected to Low-Voltage Systems: Characteristics and Test Methods,” Class II.

(l)		Spare Items

Spare items for the facilities are shown in Table 53-15.

Table 53-15: Spare Items

| No | Item | Quantity |
| --- | --- | --- |
| 1 | Fuses | 100% |

(4)	Monitoring Control Panel

(a)	Device Structure

This facility shall consist of the following devices.

Transmission Control Unit

Power Supply

Operating Control

Display

(b)	Structure

(i)	The housing must be electronically and mechanically sturdy, with a design adhering to JIS C-6010-2.

(ii)	The housing must be an indoor free-standing enclosed type, with a design making maintenance inspections easy.

(iii)	The elements of this facility which will be installed indoors (excluding hard disks and recording media) must have earthquake resistance adhering to JEM TR144 “Earthquake Resistance Design Guidelines for Power Distribution Panels/Control Panels,” with an earthquake resistance class equivalent to “General Buildings –Important Panels” Class A.

For design purposes, horizontal seismic intensity must be at least 0.6 for the first floor and basement, at least 1.0 for medium floors, and at least 1.5 for top floors and roof.

However, vertical seismic intensity for design purposes shall not adhere to JEM-TR144, but shall be half of the horizontal seismic intensity for design purposes.

(iv)	Electrical noise must meet the VCCI Class A technological standard.

(v)	The upper portion of the front panel of the housing must include a graphic panel.

(vi)	The housing must include a management nameplate.

(vii)	Housing dimensions shall be 700 mm in width × 1950mm in height × 500mm in depth.

However, this excludes protruding elements.

(viii)	Housing shall be made from the materials shown below:

Housing Body	Protective Steel Plate SPCC (JIS G 3141) 1.6t

Doors	Protective 	Steel Plate SPCC (JIS G 3141) 2.3t

(ix) 	Housing coating shall consist of base treatment followed by primer and a middle coat applied to both interior and exterior. The exterior shall be bake-finished with a double coating of melamine resin paint, while the interior shall be finished with at least one coat. Coating color and thickness are shown in Table 53-16.

Table 53-16: Coating Color and Thickness

|  | Coating Color | Thickness |
| --- | --- | --- |
| Exterior | Munsell 5YR2/1.5 7 matte | > 60μm |
| Interior | Munsell 5YR2/1.5 7 matte | > 35μm |

(c)		Main Capacities

(i) 	Display Control Signal Receipt Response Time: 	Regarding display control signal receipt response time, the monitoring control panel processing time between receipt of a display control signal by the upper station and a receipt completed signal being sent to the upper station shall be less than three seconds.

(ii)	Display Control Signal Processing Time: Regarding display control signal processing time, the monitoring control panel processing time between receipt of a display control signal from the upper station and display control signal data being sent to the information board shall be less than three seconds.

(iii) 	Status Monitoring Signal Processing Time: Regarding status monitoring signal processing time, the monitoring control panel processing time between receipt of a status monitoring signal from the information board and a status monitoring signal being sent to the upper office shall be less than three seconds.

(d)	Number of Registered Display Items

Display items can be expressed as a combination of four separate items: area 1, area 2, cause and action, and more than 1023 must be able to be registered communally to all connected information boards.

(i)	Number of Registered Character Codes and Symbol Pattern: Character codes may be registered. In addition, more than 30 symbol patterns must be able to be registered.

(e)		Functions and Specifications

(i)	Transmission Control Unit

The transmission control unit shall function to send display control signals and status monitoring signals received from the upper station to each information board, and send status monitoring signals received from the information boards to the upper station.

The transmission control unit shall function to send display control signals and test control signals received from the operation control to each information board, and send status monitoring signals received from the information boards to the operation control.

The transmission control unit shall function to send monitoring control signals received from the operation control to each information board, and send status monitoring signals received from the information boards to the operation control.

The transmission control unit shall function to convert display item numbers and symbols received from the upper station or operation control into display item data, and send it to the information boards.

The transmission control unit shall function to compare display item numbers and symbols received from the upper station or operation control and display item numbers sent in status monitoring signals sent from the information boards, and if a discrepancy is found, send status display monitoring item congestion to the upper station.

If information boards and the monitoring control panel recover from damage from a breakdown or blackout, the transmission control unit shall function to receive the latest display item numbers and symbols from the upper station, and send appropriate display item data to the information boards.

The transmission control unit shall function to send status monitoring items from the information board status monitoring signals to the upper station or operation control in response to a monitoring request from the upper station or operation control.

The status monitoring items to be sent are shown in Table 53-17.

Table 53-17: Status Monitoring Items

| Item | Content |
| --- | --- |
| Test | Under test control from the monitoring control panel |
| Breakdown | Power supply breakdown, unit breakdown and board breakdown |
| Manual | Information board (controller unit) is set to test mode (manual operation) |
| Congestion | Transmission error such as unregistered signal and control processing error, etc. |

The transmission control unit shall function to monitor the information boards within a period of three seconds. In addition, if an anomaly is found in the information board status, the transmission control unit shall function to send status monitoring items to the upper station.

Blackout-Response Functions. In response to a blackout of less than 250ms, the transmission control unit shall operate as it would at times of normal power.

(ii)	Specifications

No. of connected information boards

DL-Type Information Board	2 boards

EL-Type Information Board	6 boards

(iii)	Operation Control

Functions: Operation control shall serve the following operation functions:

- Operation control shall switch between “remote” and “manual.”

- “Remote” mode means that the information boards are controlled and monitored from the upper station.

- “Manual” means that the information boards are controlled and monitored from operation control.

- Operation control shall switch between “normal” and “maintenance.”

- “Normal” mode means that the information board display can be controlled and status monitoring can be conducted.

- “Maintenance” mode means that the most recent and past statuses of the information board can be checked.

- Information boards can be selected.

- Display items can be selected and controlled.

- Monitoring requests can be selected and controlled.

- Test control signals of “test start” and “test stop” can be sent.

Specifications: Operation control shall be operated via a touch panel or similar.

(iv)	Display

Functions: The display shall function to show the content of information board displays and breakdown information.

Display items, symbol patterns and status for a given tunnel section (DL-type, EL-type) shall be displayed on the same screen.

The monitor will only display when the operation control is in use.

Monitor display shall have the ability to shut off automatically, and shutoff time must be able to be set in the initial settings.

Display items must be displayed on the monitor in the same pattern and color as they are displayed on the information boards.

Specifications: The display must be in color, allowing for the number of display characters and symbol patterns to be checked.

(f)	Interface

(i)	SHDSL Modem

LAN-Side Interface

Applicable Standards	10BASE-T, 100BASE-TX

Transmission Method	IEEE802.3／IEEE802.3u

Transmission Speed	10／100Mbps

No. of Ports	4 ports

Applicable Connector	RJ-45 connector

(ii)	SHDSL-Side Interface

Applicable Standards	ITU-T G.991.2

Transmission Speed	512kbps - 5.6Mbps

Transmission Distance	10.2km (512kbps, 0.65mm, 2 wire time, theoretical value)

3.4km (5.6Mbps, 0.65mm, 2 wire time, theoretical value)

No. of Ports	at least 2 ports

Applicable Line	independently operated metal line (2W)

Applicable Connector	RJ-11

(g)	Operation Conditions

Conditions under which these facilities can be operated normally are shown in Table 53-18.

Table 53-18: Classification of Operation Conditions

Operation Conditions

IEC60721-3-3 Environmental Conditions 3K3/3Z1/3B1/3C1/3S2/3M2 K: Weather Conditions Z: Special Weather Conditions B: Wildlife Conditions C: Chemically Active Substances S: Mechanically Active Substances M: Mechanical Conditions

For details, refer to IEC 60721-3-4 “JIS C 60721-3-4 [Classification of Groups of Environmental Parameters and their Severities]”.

(h)	Operation Conditions

(i)	Power Supply: 	AC single-phase two-wire 100V±10% 60Hz

(2)	Power Consumption: 	Power consumption for this facility is = 	< 1.0KVA

(i)	Insulation Resistance

Insulation resistance for this facility must be at least as high as the values standardized in JIS C 0704, and measuring locations, etc. are shown in Table 53-19.

Table 53-19: Insulation Resistance Measurement Locations and Measurement Conditions

| Measurement Locations | Measurement Conditions |
| --- | --- |
| Between power supply terminal and grounding terminal | With earth removed |
| Between both transmission terminals | With external lines cut off |
| Between one transmission terminal and grounding terminal | With earth removed |

(j)	Voltage Resistance

Voltage resistance for this facility must be at least as high as the values standardized in JIS C 0704, and measuring locations, etc. are shown in Table 53-20.

Table 53-20: Voltage Resistance Measurement Location and Measurement Conditions

| Measurement Location | Measurement Conditions |
| --- | --- |
| Between power supply input and housing | With control system and earth removed |

(k)		Spare Items

Spare items for the facilities are shown in Table 53-21.

Table 53-21: Accessories

| No | Item | Quantity |
| --- | --- | --- |
| 1 | Fuses | 100％ |

(5)	Emergency Telephone

(a)	Emergency Telephone

(i)	Structure

The emergency telephone shall be wall-mounted and installable on the back of the emergency telephone storage box.

Operation and maintenance inspections must be easily performed from the front, and the design must be equivalent to or better than JIS C 0920 (protection classes for the exterior of electronic devices) IPX2 (Anti-dust: not specified, waterproofing: level 2).

The housing must be made of JIS G 3141 (cold-rolled steel sheet and steel strip) SPCC t1.6 or better material.

The housing must be coated with one coat of polyester resin or equivalent or better material with a powder coating finish, and the coating color must be manufacturer standard.

Accessory hardware such as hinges, washers, hangers, etc. must be stainless steel.

(ii)	Functions and Standards

A receiver, reporting push-buttons, operation instruction plate, and management name plate (device name, model, serial number, manufacturing year and month, and manufacturer) must be included. The management name plate must be mounted in an easily visible location. Mounting hardware must also be included.

- There shall be no more than four reporting push-buttons, and the reporting locations shall be set to the police, fire department, and highway manager.

The hook switch shall be opened and closed through the weight of the receiver.

Electronic noise shall meet VCCI Class B technological standards.

The line shall have a surge absorber with surge current resistance of at least 1250A (8/20μs).

The following basic functions shall be included:

- Call Function: A call shall be made automatically when the receiver is unhooked, the dial tone sounds, and a reporting button is pressed.

- Call Receipt Function: The ringer will sound when an incoming call is received, and unhooking the receiver shall allow the parties on each end of the call to speak to one another.

- Lock-Out Function: This function shall prevent a single terminal from monopolizing the line for more than a set time.

- A timer installed within the housing (or lockout signal receipt) will disconnect the emergency telephone from the line. In addition, hanging the receiver on the hook will return operation to normal.

- Contact Signal Function: A contact signal output shall be sent out when the receiver is place on the hook or taken off the hook.

- Signal Selection Function: This function shall allow a DP signal (20 pulse per second system) or PB signal to be selected. It must include an easy-to-operate toggle switch.

- Anti-Noise Function: This function shall reduce ambient noise, and make the conversation easier to hear in the tunnel road environment.

The following maintenance functions must be present.

- Volume Adjustment Function	Receiver volume must be easily adjustable.

- Number Registration Function: Reporting numbers shall be easily set (register/edit/delete) via a switch installed on the housing, etc.

Power Supply System: station power supply DC -48V

(b)	Emergency Telephone Storage Box (Wall-Mounted Type)

(i)	Structure

Must be a wall-mounted type which can be mounted from the back, with an emergency telephone storage box in which to store the emergency telephone, a display lamp, and a power supply.

Maintenance inspections must be easily performed from the front, and the design must be equivalent to or better than JIS C 0920 (protection classes for the exterior of electronic devices) IPX5 (Anti-dust: not specified, waterproofing: level 5).

The housing must be made of JIS G 4305 (cold-rolled steel sheet and steel strip) SUS304 t1.5 or better material.

The housing must be finish-coated with two coats of urethane resin paint or equivalent or better material, and the coating thickness must be at least 50μm. Coating color must be Munsell N7.0 with gloss.

(ii)	Functions and Standards

Emergency Telephone Signboard Display Content. Emergency telephone signboard display content is shown below:

- Background:  Green

- “Emergency Telephone” characters: White (characters shall be rounded gothic) or “SOS” characters: White (characters shall be rounded gothic)

- Telephone Mark:  Black (mark shall be surrounded with a white field)

- The display lamp shall use an internally-illuminated white acrylic panel, with an LED light source (< 15VA). The content of the display shall read “Emergency Telephone” (green characters, rounded gothic font) or “SOS” (green characters, rounded gothic font)

Power Supply

An MCCB shall be installed, including space for a step-down transformer.

Voltage used shall be single-phase two-wire 100V±10% 50/60Hz

(c)	Emergency Telephone Storage Box (Box-Type)

(i)	Structure

The telephone box must ensure safety and clear speaking during calls, and include an emergency telephone rack on which to store the emergency telephone. In addition, space must be provided for mounting push-button reporting devices (Type II) and a panel explaining push-button reporting.

Maintenance inspections must be easily performed, and the design must be equivalent to or better than JIS C 0920 (protection classes for the exterior of electronic devices) IPX3 (Anti-dust: not specified, waterproofing: level 3).

The materials used shall meet the following standards.

(ii)	Functions and Standards

A management name plate (device name, model, serial number, manufacturing year and month, manufacturer), and management display plate (acrylic plate, etc.) must be mounted in an easily visible location. Must include frame and mounting hardware.

Doors must be easy for telephone users to open. After use, they must automatically shut firmly, and not open on their own. The front of the doors must bear the lettering “Emergency Telephone” (white, rounded gothic font) or “Emergency Telephone SOS” (white, rounded gothic font).

The light source for the internal lighting shall be LED (< 40VA), and must include an MCCB and power supply transformer.

- (a) Input Voltage	single-phase two-wire 100V±10％

(d)	Digital Electronic Switchboard (PBX)

(i)	System Outline

The system shall be made up of the electronic switchboard and telephones, and shall be installed for the following calls.

Calls between the emergency telephones and the administrative office phone

Internal extension-to-extension calls

(ii)	Structure

The housing must have superior strength and rust-proofing.

Coating color shall be manufacturer standard.

(iii)	Functions and Standards

Telephone Switchboard Body

- Control System	stored program control system

- Processing System	distributed control system

- Speech Path System	time-division PCM system

- Office-Line Response System

- office-line relay

- Direct-line system

- Dial-in System

- Direct-in-line system

(v)	Speech Path	time-division 1-stage speech path

(vi)	Controller	at least 32-bit microprocessor

(vii)	Main Recorder	compact flash

(viii)	Input-Output Unit	telnet client

(ix)	Redundancy	two-layer

Two-layer redundancy must include an operational unit which is always switched on, and a backup unit which only switches on if the operational unit breaks down. There must be no cyclic switching between operational and backup.

(x)	Cooling Conditions:  fan-modulated forced-air cooling system (long-life fan)

(xi)	Line Conditions:

General Internal Line:  Series resistance < 1200Ω (DP), < 800Ω (PD) (including resistance inside the telephone itself)

Leakage Resistance:  20kΩ

(xii) 	Environmental Conditions

Temperature	0 to 40°C

Humidity	20 to 80% RH (no condensation)

(xiii)	Power Supply Voltage	AC operation single-phase two-wire 100V±10% 50/60Hz

(xiv)	Line Structure

Line Type	Installation

Emergency Telephone Line	2 Lines

(e)	Monitor Panel

(i)	Design

Must be an indoor wall-mounted type, on which operation and maintenance inspections can easily be performed from the front, and must be designed with special consideration for electrical safety.

The housing shall be steel plate equivalent to or better than JIS G 3141 (cold-rolled steel sheet and steel strip) SPCC t1.2.

Housing coating shall be bake-finished with least two coats of melamine resin paint or equivalent or better material. Coating thickness must be at least 50μm. Coating color shall be manufacturer standard.

(ii)	Functions

Performance

- Monitoring items are shown below:

- Automatic Reporting	(lamp displays red)

- Manual Reporting	(lamp displays red)

- Information Board Interlocking in Progress: (lamp displays red)

- Information Board Testing in Progress:  (lamp displays orange)

- When a warning signal of “automatic reporting” or “manual reporting” is received, the associated monitoring lamp and “information board interlocking in progress” shall illuminate, and a warning buzzer will sound, which can be turned off with the warning buzzer off-switch.

- If a blackout occurs, blackout backup batteries will sustain normal operation for 40 minutes.

- If information boards are being tested, “information board testing in progress” shall display on the monitor, and the buzzer will not sound.

Electrical Standards

- Power Supply

- Input:	single-phase two-wire 100V±10% 50/60Hz

- Capacity:	<100VA

Transmission Lines: 	Signal delivery to/from the monitoring control panel shall be a no-voltage contact.

Voltage resistance and insulation resistance

- Power Supply Input Terminal – Housing:  AC1000 V  for one minute; >10MΩ on 500 V Insulation Resistance Meter

- Signal Input Terminal – Housing:  >1.5MΩ on 250 V Insulation Resistance Meter

- Between Signal Input Terminals:  >1.5MΩ on 250 V Insulation Resistance Meter

(f)	Spare Items

Spare items for the facilities are shown in Table 53-22.

Table 53-22: Accessories

| No. | Item | Quantity |
| --- | --- | --- |
| 1 | Fuses | 100％ |

(6)	Evacuation Guidance Display/Display Lights

(a)	Applicable Standards / Types

Any items not expressly stipulated in these specifications shall adhere to the following standards.

(i)	Applicable Regulations and Standards

International Electrotechnical Commission (IEC) Recommended Standard

International Standards (ISO)

International Commission on Illumination (CIE) Standards

Japanese Industrial Standards (JIS)

Japan Lighting Manufacturers Association Standards (JIL)

Electrical Appliance and Material Safety Law (1961, Law No. 234)

Other related laws

(ii)	Types

Display board/ display lamp types are shown in Table 53-23.

Table 53-23: Display Board / Display Lamp Types

| Type | Item | Description |
| --- | --- | --- |
| S1(A) | Guidance Display Board (Surface Mounted) | Shall be mounted on tunnel wall surfaces except for emergency parking strip, and shall display the direction and distance to the tunnel mouth or evacuation connector tunnel. |
| S1(B) |  | Shall be mounted on the tunnel wall surfaces of the opposite traffic lane from the evacuation connector tunnel, indicating the presence of the evacuation connector tunnel. |
| S3 | Emergency Exit Display Lamp | Shall be mounted on the tunnel wall surfaces of the opposite traffic lane from the evacuation connector tunnel, indicating the presence of the evacuation connector tunnel. |
| S4 | Emergency Exit Display Lamp (With Warning Light) | Shall be mounted on tunnel wall surfaces next to the entrance to the evacuation connector tunnel, indicating the presence of the evacuation connector tunnel. |
| S5 | Warning Lamp | Shall be mounted on tunnel wall surfaces next to the entrance to the evacuation connector tunnel, indicating the presence of the evacuation connector tunnel while warning against sudden movements out into the traffic lane. |
| S6 | Emergency Parking Strip /Emergency Telephone Display Lamp (Double-Sided Display) | Shall be mounted on tunnel wall surfaces near the face-to-face traffic tunnel emergency parking strip, indicating the presence of the emergency parking strip and emergency telephone. |

However, the display board / display lamp light source shall be LED.

(b)	Structure

(i) 	Body and Waterproofing Functions:  The structure must be equivalent to or better than JIS C 0920 “[protection classes (IP codes) for the exterior of electronic devices] 3. Performance” IPX5.

(ii)	Body:  Must be made of cold-rolled stainless-steel sheet.

(iii)	Lamps must have superior corrosion resistance, and consideration must be taken regarding crevice corrosion, stress corrosion, and electrolytic corrosion from contact between different metals.

(iv)	Lamps must be easily and sturdily mounted on tunnel walls either directly or using mounting hardware.

(v)	Display boards / display lamps must be mounted in locations where the light sources and mounting will not loosen, disconnect, or fall due to vibration stimulation during use or during inspections.

(vi) 	Display boards / display lamps must be easily and safely opened and shut for exchange of light sources and maintenance inspections.

(vii) 	The front surface of light fixtures must not have any projections which could interfere with cleaning using spinning brushes, etc.

(viii) 	Power supply shall be fed into the light fixtures either via direct cable or via cable tube.

(ix) 	Bolt holes for the mounting and mounting hardware must be vertically and horizontally adjustable.

(x) 	Display board / display lamp interior must allow input power from batteries to be shut on or off during maintenance inspections and parts replacement.

(xi) 	Fixture interiors shall include terminal blocks to connect to outside power lines.

(xii)	Fixture interiors shall include grounding terminals.

(xiii)	Batteries stored in display boards / display lamps must have functions equivalent or superior to “JIS C 8705 [cylindrical sealed nickel-cadmium storage batteries]”.

(xiv)	Translucent covers must have functions equivalent or superior to float-tempered glass under “JIS R 3206 [Tempered Glass]” standard.

(xv)	Display board / display lamp insulation resistance and voltage resistance shall be as stipulated in “JIS C 8105-1 [Lighting Fixtures – Part 1: General Rules for Safety Requirements]　Chapter 10　Insulation Resistance and Voltage Resistance.”

(c)		Optical Performance

Display Board / Display Lamp

- The initial value for average brightness of the white portions of the display boards must be at least the value of the Table 53-24 value divided by the luminous flux maintenance rate shown in Clause 6.5: “Specifications / Operation Conditions”.

Table 53-24: Brightness (cd/m2)

| Type | Item | Average Brightness |
| --- | --- | --- |
|  |  | Front |
| S1(A) | Guidance Display Board (Surface-Mounted Type) | 130 |
| S1(B) |  |  |
| S2(A) | Guidance Display Board (Embedded Type) | 130 |
| S2(B) |  |  |
| S3 | Emergency Exit Display Lamp | 220 |
| S4 | Emergency Exit Display Lamp (With Warning Lamp) | 220 |
| S5 | Hazard Warning Lamp | 200 |
| S6(A) | Emergency Parking Strip・Emergency Telephone Display Lamp (One-Sided) | 150 |
| S6(B) | Emergency Parking Strip・Emergency Telephone Display Lamp (Two-Sided) | 150 |

Display board/display lamp light distribution is stipulated in “JIL 5502 [Emergency Lighting and Guideline for Evacuation System for Equipment Technical Standards]”.

(d)	Functions and Specifications

(i)	Functions

Mounting Function: Display boards / display lamps must be sturdily mounted on tunnel wall surfaces.

Storage Functions: Light sources and lamps must be stored within the light fixtures.

Maintenance Functions: Internal maintenance inspections and light source replacement must be performed easily while display boards / display lamps remain mounted on tunnel walls.

Display Functions: Display board display content must be easily readable when the light source is illuminated.

Blackout Backup Functions:

- The instant commercial power blacks out, power supply will switch to backup batteries which will keep lamps illuminated for at least 30 minutes.

- Blackout conditions are shown below:

- The average brightness of the white portion of the display board surface of display boards / display lamps must be at least 50% of the value shown in Table 53-24.

- S1 display board / display lamp luminous intensity must be at least 50% at an 87 degrees horizontal angle from the front surface.

- Warning lamp luminous intensity shall be at least 70% at a three degrees horizontal angle relative to the front surface of the display board.

(e)	Specifications / Operation Conditions

(i)	Specifications

Display Board/Display Lamp Display Color and Dimensions:  Display board/display lamp color and dimensions are shown in the design diagrams.

Warning Lamp Dimensions and Mounting Locations:  Warning lamp dimensions shall be greater than 90mm in diameter, and they shall be mounted on the lower portion of the display lamps.

Luminous Flux Maintenance Rate at Expected End of Light Source Lifespan:  The luminous flux maintenance factor at the expected end of light source lifespan must exceed the following values:

- Luminous Flux Maintenance Rate at Expected End of Light Source Lifespan

| Light Source | Expected Lifespan (Hours) | Lumen Maintenance Factor |
| --- | --- | --- |
| LED | 4.0×104 | 0.5 |

(ii)	Operation Conditions

Conditions under which the display board / display lamps can function properly are shown in Table 53-25.

Table 53-25: Classification of Operation Conditions

| Type | Item | Average Brightness |
| --- | --- | --- |
|  |  | Front |
| S1(A) | Guidance Display Board (Surface-Mounted Type) | 130 |
| S1(B) |  |  |
| S2(A) | Guidance Display Board (Embedded Type) | 130 |
| S2(B) |  |  |
| S3 | Emergency Exit Display Lamp | 220 |
| S4 | Emergency Exit Display Lamp (With Warning Lamp) | 220 |
| S5 | Hazard Warning Lamp | 200 |
| S6(A) | Emergency Parking Strip・Emergency Telephone Display Lamp (One-Sided) | 150 |
| S6(B) | Emergency Parking Strip・Emergency Telephone Display Lamp (Two-Sided) | 150 |

For details, refer to IEC 60721-3-4 “JIS C 60721-3-4 [Classification of Groups of Environmental Parameters and their Severities]”.

However, the temperature of the air surrounding the facility shall be as follows:

Temperature of the air surrounding the facility =  -10°C to +40°C

(iii)	Power Supply

The standard input voltage for these facilities is shown below:

Three-Phase Three-Wire Type	415V±10% (50Hz)

(iv)	Load Capacity

The load capacity of the sign board / display lamps is shown below:

Sign Board / Display Lamp Load Capacity

| Type | Load Capacity (VA) |
| --- | --- |
|  | LED |
| S1(A) | 50 |
| S1(B) | 50 |
| S3 | 30 |
| S4 | 35 |
| S5 | 30 |
| S6(B) | 40 |

(7)	Quality Management

The department of the manufacturing company directly involved with manufacture of the devices (final inspection department, etc.) must have an ISO9001-certified quality management system (engineering, development, manufacture, installation, and utility services quality guarantee model), or must have a quality management system and structure under an auditor who has equivalent certification.

5400.	REMOTE MONITORING AND CONTROL SYSTEM

(1)	Description

(a)	System Components

The Tunnel Management System shall consist of the following facilities and devices.

Monitoring control equipment

FM radio rebroadcasting system (including loudspeaker equipment)

Radio communication auxiliary system (including VHF radio for road administrator)

CCTV camera equipment

(b)	Applicable Standards

The System shall comply with these Specifications, and laws, regulations, rules and specifications listed here below.

Applicable Standards

Part 5 CCTV Facilities in “Standard Design Specifications Vol. 8 Communications Facilities” (NEXCO RI, July 2014)

Part 7 FM Radio Rebroadcasting Facilities in Tunnels in “Standard Design Specifications Vol. 8 Communications Facilities” (NEXCO RI, July 2014)

Part 7 Digital Mobile Radio Communication Facilities in “Standard Design Specifications Vol. 8 Communications Facilities” (NEXCO RI, July 2017)

“Standard Specifications, etc. for FM Radio Rebroadcasting Facilities in Tunnels”, Specification No. 17212 (NEXCO RI, July 2017)

“Standard Specifications, etc. for CCTV Facilities”, Specification No. 17219 (NEXCO RI, July 2017)

“Standard Specifications, etc. for Intelligent Remote-Control Monitoring Equipment Vol. 2”, Specification No. 17210 (NEXCO RI, July 2017)

“(Draft) Specifications for CCTV Facilities” (Ministry of Land, Infrastructure, Transport and Tourism, January 2017)

“(Draft) Specifications for Radio Rebroadcasting Facilities in Tunnels (with interruption function)” (Ministry of Land, Infrastructure, Transport and Tourism, January 2017)

“Standard Specifications for Digital Land Mobile Communication Systems (K-λ)”, MLIT Specification for Communication Facilities No. 55 (Ministry of Land, Infrastructure, Transport and Tourism, October 2015)

“Degrees of Protection Provided by Enclosures” (IP Code), IEC 60529

“Degrees of Protection Provided by Enclosures for Electrical Equipment” (JIS C 0920), Japanese Industrial Standards

For any matters referred to in multiple documents, these Specifications shall prevail.

The System shall be manufactured, installed, tested, and test-operated under the quality assurance and quality control system in compliance with ISO 9001. The manufacturers are required to have a copy of ISO 9001 issued by a public, independent organization.

(2)	Basic Requirements

(a)	Basic Design

The Tunnel Management System is a system that shall be installed in the Control Office of the East Electric Room, and monitor and control disaster prevention facilities in the tunnel (such as emergency, ventilation, lighting and other facilities).

The System shall enable operators to monitor the real-time states of facilities and alerts from the operation terminal and large screen display in the Control Office. It shall also provide road users with appropriate information through appropriate road boards and radio broadcasting.

(b)	Durability

The system shall be operated 24 hours a day, 365 days a year, the hardware must be durable for continuous operation.

The System shall be operated 24 hours a day and 365 days a year. The hardware shall be reliable enough for continuous operations.

The integrated management server shall represent the core of the System, and secure redundancy so that defect of any component shall not adversely affect the entire System. In case of any trouble with the operation system hardware of the integrated management server or application programs to be created, the backup system hardware shall automatically take over the operations for continuous operations of the entire System.

(c)	System Extensibility

The System shall be easily linked to other systems, and have additional functions for possible future system extensions.

It shall also easily incorporate additional facilities through revisions to relevant definitions and settings.

(d)		Power Supply

The Telecommunication Machine Room in the East Electric Room, and equipment in the Control Office shall be powered at 100V AC via the uninterruptible power system. Other equipment shall be compatible with 220V AC, single phase 50Hz.

(3)	Monitoring Control Equipment

(a)	Application

This section shall apply to components, etc. of the monitoring control equipment to be installed in the tunnel (hereinafter referred to as the “Equipment”).

(b)	System Overview

The system overview of the Equipment shall be as follows.

The Equipment shall:

•	Generate the present state information about data from slave stations, and chronologically store and process various data necessary to present the history information.

•	Monitor changes in the state of facilities and systems in the tunnel, and judge whether to issue alerts.

•	Arithmetically process measurements recorded regularly and when necessary for facilities and systems in the tunnel, and aggregate data on daily and monthly bases.

•	Arithmetically process and present search results of information about equipment monitored and equipment, for which control order is made.

•	Issue alerts in response to the results of judgments.

•	Deliver information about the tunnel to the website, and generate and process the contents.

•	Display all the camera views and screens (screens to monitor and control the state of the tunnel) generated on the integrated management server on the large screen display.

(c)	Service Space

The Equipment shall be installed in the East and West Electric Rooms, both of which are indoors.

(d)	Ambient Conditions

•	Temperature: indoor,	0°C to 40°C

However, 10°C to 35°C for general information devices

•	Humidity: indoor,	10 to 85%RH

However, 20 to 80%RH (non-condensing humidity) for general information devices

(e)	Structures

Individual server equipment and racks shall have the following structures.

•	The Equipment shall be made of durable and rust preventive steel.

•	Stand-along devices shall be earthquake-resistant to prevent accidents due to horizontal displacement, falling or drop of any parts.

•	Devices shall be mounted on steel racks, which shall be fixed directly and horizontally on concrete floors.

•	Devices to be placed on the free access floor shall be fixed with bolts on special racks, which shall be placed in a hole created in the floor. Special racks shall have a structure, in which bolts used to fix the devices on the concrete floor are visible.

(f)	Components of the Equipment

The Equipment shall consist of the following components and devices.

Table 54-1: Components of the Monitoring Control Equipment

| Name | Specifications | Unit | Q’ty | Notes |
| --- | --- | --- | --- | --- |
| Integrated management server equipment |  |  |  |  |
| Processing Server #1 (integrated management server) |  | unit | 1 |  |
| Processing Server #2 (integrated management server) |  | unit | 1 |  |
| Maintenance console / KVM switch |  | unit | 1 |  |
| Layer 3 Ethernet switch | 48 or more ports | unit | 1 |  |
| Server rack | W700×H2000×D1000 | unit | 1 |  |
| Facility management transmission equipment |  |  |  |  |
| PLC |  | unit | 1 |  |
| Media converter |  | unit | 1 |  |
| Cabinet | W600×H2000×D600 | unit | 1 |  |
| Junction terminal equipment #A | W600×H2000×D600 | unit | 1 |  |
| Facility management transmission equipment #2 | W600×H2000×D600 | unit | 1 | West Electric Room |
| Large Screen display | Consists of four screens | set | 1 |  |
| Multi-vision controller | Mounted on large screen display | unit | 1 |  |
| Layer 2 Ethernet switch | 24 or more ports Mounted on large screen display | unit | 1 |  |
| Operation terminal (Disaster prevention system / Facility system / Transportation system) |  | unit | 1 |  |
| Desk (OA desk) |  | unit | 1 |  |

(g)	Specifications of Components

Components of the Equipment shall conform with the following specifications.

(i)	Integrated management server equipment

Integrated management server: The server shall have a dual structure consisting of operation and backup systems. In case of any trouble with the operation system hardware or application programs to be created, the backup system shall automatically take over their operations for continuous operations of the entire System.

- Processing server #1 (operation system)

- CPU: Xeon E5-2620 v4 processor 2.10GHz x 2 or equivalent

- Main memory: 32GB or larger

- Hard disk: 300GB×3 (RAID 1, with hot spare) or more

- Optical drive: DVD-ROM

- LAN interface: 10/100/1000BASE-T × 4 or more ports

- OS: Linux, Windows or equivalent

- Structure: Rack-mounted

- Power: AC100V 50/60Hz (dual power supply)

- Processing server #2 (backup system)

- Equivalent to the specifications of Processing Server #1

- Functional specifications (software)

- File processing: The server shall generate the present state information about data from slave stations, and chronologically store and process various data necessary to present the history information.

- Facility monitoring processing: The server shall monitor changes in the state of facilities and systems in the tunnel, and judge whether to issue alerts.

- Measurement operation processing: The server shall arithmetically process measurements recorded regularly and when necessary for facilities and systems in the tunnel, and aggregate data on daily and monthly bases.

- Individual control processing: The server shall conduct interlocking processing of control and order information to facilities in the tunnel. It shall deliver control outputs to facilities on site via slave stations.

- History processing: The server shall arithmetically process and present search results of information about equipment monitored and equipment, for which control order is made.

- Alert output processing: The server shall issue alerts in response to the results of judgments.

- Telecommunication processing (for PLC): The server shall, with PLC and network connection, process reception and transmission of monitoring and control information.

- -Information to and from PLC shall be in accordance with Table 54-3 “Items to Be Handled by Monitoring Control Equipment (East and West Electric Rooms)”.

- Telecommunication processing (for emergency facilities): The server shall, with emergency facilities and network connection, process reception and transmission of information for road display boards.

- Telecommunication processing (for FM radio rebroadcasting system):

-	The server shall, with FM radio rebroadcasting system and network connection, process reception and transmission of monitoring information.

-	Information to and from the FM radio rebroadcasting system shall be as follows:

・	Information to be received:  State monitoring information

・	Information to be transmitted:  Fire interlocking signals

- Telecommunication processing (CCTV camera equipment): The server shall, with CCTV camera equipment and network connection, process communications of monitoring information and the state of CCTV camera.

- Telecommunication processing (for multi-vision controller): The server shall, with multi-vision controller and network connection, process reception and transmission of information, and provide information to display on the large screen display.

- Web processing:

-	The server shall deliver information about the tunnel on the website, and generate and process the contents.

-	Information to be provided shall be for monitoring, control and measuring. Screen types are listed in Table 54-2.

-	The language used for web processing shall be English.

Table 54-2: Screen Types of Monitoring Control Equipment

| Type | Contents |
| --- | --- |
| Current state diagram | Schematic diagrams display monitoring data of the tunnel. |
| Current state table | Tables give lists of monitoring data of the tunnel in terms of facility and system. FM radio rebroadcasting system / CCTV camera equipment Emergency facilities Fire extinguishing facilities / power receiving / transforming facilities / lighting facilities / ventilation facilities/ emergency telephone facilities VHF radio for road administrator Other facilities |
| History | History shows lists of facility, alarm and system logs. |
| Measurements | Measurements show lists of measurements of power receiving and distributing facilities, and ventilation facilities. Measurements shall show lists of their current values, daily compilation and monthly compilation. |
| Facility control | Guidance on control and operation The lamps of operable buttons flash according to the monitoring state. Operators shall press buttons for intended controlling. |

- User management: The control and maintenance settings shall be subject to access control by IP addresses.

- Maintenance settings (Stop processing of data distribution to other devices): The server shall have a function of stopping data distribution to other devices for maintenance and inspection.

- Maintenance console / KVM switch: Maintenance console and KVM switch shall be used to switch display operations of Processing Servers #1 and #2 for maintenance of the integrated management server. The specifications are as follows:

- Display: 17-inch WXGA or equivalent; Minimum 1280×768, full color

- Input device: Keyboard

- Pointing device: Touchpad with 3 buttons

- CPU switcher: 8 or more input ports, 1 or more output ports

- Form: Rack-mounted

- Power: AC100V 50/60Hz

- Power consumption: 100W or below

- Layer 3 Ethernet switch: The switch shall be used to transmit IP data, and control routing of multicast images.

- Structure: Rack-mounted

- Backplane capacity:  170 Gbps or more

- No. of interfaces:  10/100/1000BASE-T interface x 48 or more ports

- Compatible standards:  10BASE-T:  IEEE802.3

100BASE-TX:	IEEE802.3u

1000BASE-T:	IEEE802.3ab

- Packet transmission capacity:  maximum 100Mpps or more

- Routing protocol:	OSPF

Software compatible with the protocol mounted

- IP multicast: Supporting IGMPv2, IGMPv3, PIM-Sparse mode, and PIM-SSM

Operable as BSR and C-BSR

Operable as RP and C-RP

- Priority control: The switch is capable of priority control of traffics in accordance with COS, IP precedence and DSCP value of IEEE802.1p.

- VLAN: The switch can support 1000 or more functions.

The switch can support VLAN for each port.

It can also configure tag VLAN (IEE802.1Q).

- Fault bypass: The switch can support independent spanning tree protocol for each VLAN (including tag VLAN).

- Multicast: The switch shall transmit multicast packets only to relevant ports.

(Function equivalent to IGMP snooping)

- Management protocol: SNMP (v1, v2, v3)

- Power: AC100V 50Hz/60Hz (dual power supply)

- Maximum power consumption: approx. 250W

- Server rack

- Structure:	Indoor rack

Stand-alone, steel

- External dimensions:	Width: 700mm

Height: 2000mm

Depth: 1000mm

(except protruding parts)

(ii)	Facility Management Transmission Equipment

PLC:

- PLC shall input and control changes in the state of monitoring information of facilities in the tunnel, and process reception and transmission of monitoring and control information with devices at the higher rank station.

- Items to be handled: Table 54-3 lists items to be handled by the equipment. The number of items in Table 54-3 refers to the total number of items to be monitored or controlled at the East and West Electric Rooms.

Table 54-3: Items to Be Handled by Monitoring Control Equipment (East and West Electric Rooms)

| Item | Type | No. (maximum No.) | Interface |
| --- | --- | --- | --- |
| Emergency facilities | Monitoring | － | (*) Transmission (TCP/IP), contents of VMS display |
| Fire extinguishing facilities | Monitoring | 128 | Contact |
|  | Monitoring | BCD3 digits | Contact |
| Power receiving / transforming facilities | Monitoring | 128 | Contact |
| Lighting facilities | Monitoring | 64 | Contact |
| Ventilation facilities | Monitoring | 128 | Contact |
| Emergency telephone facilities | Monitoring | 32 | Contact |
| VHF radio auxiliary equipment | Monitoring | 8 | Contact, monitoring information from base station |
| FM radio rebroadcasting system | Monitoring | － | (**) Transmission (TCP/IP), |
| CCTV camera equipment | Monitoring | － | (***) Transmission (TCP/IP), |
| Other facilities | Monitoring | 32 | Contact |
| Power receiving / transforming facilities | Measuring | 8 | DC4-20mA |
| Ventilation facilities | Measuring | 6 | DC4-20mA |
| Emergency facilities | Control | － | (*) Transmission (TCP/IP), control of VMS |
| Fire extinguishing facilities | Control | 16 | Contact |
| Power receiving / transforming facilities | Control | 64 | Contact |
| Lighting facilities | Control | 32 | Contact |
| Ventilation facilities | Control | 32 | Contact |

VMS: Variable Message Signboard

(*) Communications with the emergency facilities shall be made through the integrated management server and network connection, rather than via PLC.

(**) Communications interfaced with the FM radio rebroadcasting system shall be made through the integrated management server and network connection, rather than via PLC.

(***) Communications interfaced with CCTV camera equipment shall be made through the integrated management server and network connection, rather than via PLC.

- Interface specifications

- Communication processing unit

Interface: IEEE802.3 10BASE-T/100BASE-TX compatible

- Monitoring input unit

Interface: Continuous non-voltage, normal open

Input specifications: DC24V 4mA

- Measurement input unit

Interface: Analog signal

Input specifications: DC0 to 1mA, 4 to 20mA

- Control output unit (for fire extinguishing and ventilation facilities)

Interface: Instantaneous non-voltage, normal open (1sec or longer/pulse)

Output specifications: DC24V 1A

- Control output unit (for power receiving / transforming, and lighting facilities)

Interface: Pulse control (approx. 1 sec)

Output specifications: DC100V 0.2A or lower

- Power unit: AC100V, 50Hz/60Hz

- Functional specifications (software)

- Communication processing (Integrated management server): The equipment shall process reception and transmission of monitoring and control information through network connection with the higher rank station (integrated management server).

- Transmission of state-change signal: The equipment shall transmit only a state-change signal when the state of monitoring information changes.

- Fixed-cycle transmission: The equipment shall transmit measurement information at a fixed-cycle to the higher rank station.

- On-demand transmission: The equipment shall transmit individual control, monitoring and measurement information, and information about the state of slave stations to the higher rank station only on demand.

- Information storage: The equipment shall store history of certain states and fault signals, and transmit the data on demand from the higher rank station.

- Time adding function: The equipment shall add the time of monitoring and measuring at the internal clock of slave stations, and transmit the time with monitoring and measuring signals.

- Time synchronization: The equipment shall synchronize the clock of slave stations by calibration signals from the higher rank station.

- Health check: The equipment shall periodically send diagnostic information of the network from slave to the higher rank station to check the soundness of the network.

Media converter: Media converter shall convert signals in LAN cables (copper wire) to signals for optical fiber cables (SM).

- LAN interface: 10/100BASE-TX interface x 1 port

- Optical interface: 100BASE-FX interface x 1 port

Interface:	SC connector

Transmission distance:	within 5km

Server rack

- Structure: Indoor rack

Stand-along, steel

- External dimensions:

Width: 600mm

Height: 2000mm

Depth: 600mm

(except protruding parts)

(iii)	Junction terminal equipment #A

Terminal block:

- No. of terminals:  1000 or more

Cabinet

- Structure:	Indoor rack

Stand-along, steel

- External dimensions:	Width: 600mm

Height: 2000mm

Depth: 600mm

(except protruding parts)

(iv)	Facility management transmission equipment #2

Terminal unit:

- No. of terminals: More than the number of items to be handled with contact converter

Media converter

Media converter shall convert signals in LAN cables (copper wire) to signals for optical fiber cables (SM).

- LAN interface:	10/100BASE-TX interface x 1 port

- Optical interface:	100BASE-FX interface x 1 port

Interface:	SC connector

Transmission distance:	within 5km

PLC2

Contact converter shall convert the protocol of monitoring and control signals at the West Electrical Room for transmission on LAN cables.

- Items to be handled: Table 54-4 lists items to be handled by the equipment. The number of items in Table 54-4 refers to the number of items to be monitored or controlled at the East Electric Room.

Table 54-4: Items to Be Handled by Monitoring Control Equipment (West Electric Room)

| Item | Type | No. of items (maximum No.) | Interface |
| --- | --- | --- | --- |
| Emergency facilities | Monitoring | 0 |  |
| Fire extinguishing facilities | Monitoring | 0 |  |
| Power receiving / transforming facilities | Monitoring | 64 | Contact |
| Lighting facilities | Monitoring | 32 | Contact |
| Ventilation facilities | Monitoring | 0 |  |
| Emergency telephone facilities | Monitoring | 0 |  |
| Other facilities | Monitoring | 16 | Contact |
| Power receiving / transforming facilities | Measuring | 4 | DC4-20mA |
| Ventilation facilities | Measuring | 0 |  |
| Emergency facilities | Control | 0 |  |
| Fire extinguishing facilities | Control | 0 |  |
| Power receiving / transforming facilities | Control | 32 | Contact |
| Lighting facilities | Control | 32 | Contact |
| Ventilation facilities | Control | 0 |  |

- Interface specifications

- Communication processing unit:

Interface: IEEE802.3 10BASE-T/100BASE-TX compatible

- Monitoring input unit:

Interface: Continuous non-voltage, normal open

Input specifications:  DC24V 4mA

- Measurement input unit:

Interface: Analog signal

Input specifications: DC0 to 1mA, 4 to 20mA

- Control output unit (for power receiving / transforming facilities):

Interface: Pulse control (approx. 1 sec)

Output specifications: DC100V 0.2A or below

- Power unit: AC100V 50Hz/60Hz

- Functional specifications (software):

- Communication processing (PLC):

The equipment shall process reception and transmission of monitoring and control information through network connection with the higher rank station (PLC).

- Transmission of state-change signal:

The equipment shall transmit only a state-change signal when the state of monitoring information changes.

- Fixed-cycle transmission:

The equipment shall transmit measurement information at a fixed-cycle to the higher rank station.

- On-demand transmission:

The equipment shall transmit individual control, monitoring and measurement information, and information about the state of slave stations to the higher rank station only on demand.

- Information storage:

The equipment shall store history of certain states and fault signals, and transmit the data regularly or on demand from the higher rank station.

- Time adding function:

The equipment shall add the time of monitoring and measuring at the internal clock of slave stations, and transmit the time with monitoring and measuring signals.

- Time synchronization:

The equipment shall synchronize the clock of slave stations by calibration signals from the higher rank station.

- Health check:

The equipment shall periodically send diagnostic information of the network from slave to the higher rank station to check the soundness of the network.

- Optical terminal unit: The unit shall store optical fiber cables with at least eight cores (including backup cables).

- No. of fusion splices:  8 or more cores

- Connector:  SC connector

- No. of adapters:  8 or more

- Server rack

- Structure:	Indoor rack; Stand-alone, steel

- External dimensions:	Width: 600mm

Height: 2000mm

Depth: 600mm

(except protruding parts)

(v)	Large screen display

Large screen display shall be controlled by the multi-vision controller, and provide video images and information to the Tunnel Management Office.

Liquid crystal display

- Structure: 4 screens (2 x 2), which can be viewed as a single large monitor.

- Resolutions: 1366×768 dots or higher/screen

- Screen size: 55-inch or equivalent/screen

- Display color: 16,770,000 colors or more

- Video input: HDMI (HDCP)

- Quantity: 4 units

Display mount

- Overall dimensions: approx. W2700×H2350×D800mm

- Rack unit:

- EIA 19-inch rack or equivalent

- The rack shall have space to place devices underneath the display mount unit. The space shall have a door.

- The rack shall have a capacity for the multi-vision controller and layer 2 Ethernet switch.

- Others

- Display mount shall include metal fittings, decorative panels, and channel base.

- Display mount shall have decorative panels so that cables are unnecessarily visible from outside.

(vi)	Multi-vision controller

Multi-vision controller shall display all the camera views and screens (screens to monitor and control the state of the tunnel) generated on the integrated management server on the large screen display.

The controller can flexibly display images on the large screen display or selective component screens (location, the number of images displayed, image size, etc.).

Specifications and functions

- The controller shall collectively manage camera views and web contents for tunnel monitoring, and display them on the large screen display.

- The controller shall have an IP decoder to directly capture IP image data of camera views and display them on the large screen display.

- Display patterns shall be registered in advance.

- Display modes can be changed when necessary. (automatic patrolling, manual changeover)

Example screen layouts

Large screen display

Entire tunnel view

Camera views

Device specifications (display control unit)

- CPU: Approx. 3.50GHz x 1 or more

- Main memory: 16GB or more

- Embedded storage: SSD 250GB or higher x 1

- Optical drive: DVD-ROM

- LAN interface: 10/100/1000BASE-T x 2 or more

- Local console output: RGB, DVI or equivalent x 1 or more

- OS: Linux, Windows or equivalent

- Structure: Rack-mounted or stationary

- No. of images displayed: 17 or more

- Input connector: LAN or HDMI

- Maximum input resolution: 1920 x 1080 or more

- No. of monitor outputs: 4 or more

- Output connector: DVI-D or HDMI, display port

- Maximum output resolution:  1920 x 1080 or more

- Others:  Various display control software embedded,

Sequential display, seamless display with multiple monitors

Device specifications (LAN-DEC unit)

- Structure:  Rack-mounted, or a slot-mounted display control unit

- Input IP stream: H.264 (same as streaming method for encoder for camera)

- No. of images displayed: 17 or more

- Connector: DVI-D or HDMI, display port

- Others Capable of system expansion in response to the number of cameras for input of video images

(vii)	Layer 2 Ethernet switch

Structure: Rack-mounted

Backplane capacity: 100Gbps or more

No. of interfaces: 10/100/1000BASE-T interface x 24 ports or more

Compatible standards:

- 10BASE-T:  IEEE802.3

- 100BASE-TX:  IEEE802.3u

- 1000BASE-T:  IEEE802.3ab

Packet transfer capacity:  Maximum 70Mpps or higher

Priority control

The switch is capable of priority control of traffics in accordance with COS, IP precedence and DSCP value of IEEE802.1p.

VLAN: The switch can support 1000 or more functions.

The switch can support VLAN for each port.

It can also configure tag VLAN (IEE802.1Q).

Fault bypass:  The switch can support independent spanning tree protocol for each VLAN (including tag VLAN).

- Multicast:  The switch shall transmit multicast packets only to relevant ports. (Function equivalent to IGMP snooping)

Management protocol:  SNMP (v1, v2, v3)

Power:  AC100V 50Hz/60Hz

Maximum power consumption:  approx. 38W

(viii)	Operation terminal (disaster prevention system / facility system / transportation system)

Operators shall use web browsers to access the integrated management server, and monitor and control tunnel facilities on the web screens provided.

Operation terminals for disaster prevention, facility and transportation systems shall all have the common functions, and operators shall select screens to display.

Function:  Browsing screens to monitor and control the state of the tunnel

Controlling tunnel facilities

OS:	Windows (64bit) or equivalent

Operating environment:  24-hour continuous operation

Display language:  English

Quantity:  1 unit

(ix)	Desk (OA desk)

Type:  General-purpose product (OA desk)

External dimensions:  approx. W1200mm×H700mm×D1150mm

- (except protruding parts)

Color:  To be instructed

Others:  Device rack inclusive

Quantity:  1 unit

(4)	FM Radio Rebroadcasting System (Including Loudspeaker Equipment)

(a)	Application

This section shall apply to components, etc. of the FM radio rebroadcasting system and loudspeaker equipment to be installed in the Project (hereinafter referred to as the “Equipment”).

(b)	System Overview

The system overview of the Equipment shall be as follows.

(i)	FM Radio Rebroadcasting System

The Equipment shall receive and amplify radio broadcast signals, and rebroadcast signals through guide wires in the tunnel in normal circumstances. In emergency, it shall provide interruptive broadcast to all the channels through the memory playback unit of the Equipment or microphone.

FM radio rebroadcasting system shall follow the AF-relay method (audio relay).

Leaky coaxial cables (LCX) shall be applied to FM radio facilities inside the tunnel. LCX shall also be used for VHF radio for road administrator and other purposes.

(ii)	Loudspeaker equipment

Loudspeaker equipment shall provide interruptive announcement from the FM radio broadcasting equipment to the entrance and midsection of the tunnel. It shall have a function of monitoring and testing amplified broadcasting.

(c)	Service Space

(i)	FM radio rebroadcasting system and loudspeaker equipment: FM receiving antenna, speaker unit and microphone box shall be designed for outdoor use, and others for indoor use.

(ii)	VHF radio auxiliary equipment:  Connection terminal box, and duplexer and terminator shall be designed for outdoor use, and duplexer for indoor use.

(d)	Ambient Conditions

Temperature:

- outdoor and inside the tunnel, -15°C to 50°C

- Indoor, 0°C to 40°C

- However, 10°C to 35°C for general information devices

Humidity:  relative humidity of 85%RH or below

- However, 20 to 80%RH (non-condensing humidity) for general information devices

Wind speed:	Maximum instantaneous wind speed: 60m/s (for outdoor devices only)

(e)	Structures

Individual server equipment and racks shall have the following structures.

The Equipment shall be made of durable and rust preventive steel.

Stand-along devices shall be earthquake-resistant to prevent accidents due to horizontal displacement, falling or drop of any parts.

Devices shall be mounted on steel racks, which shall be fixed directly and horizontally on concrete floors.

Devices to be placed on the free access floor shall be fixed with bolts on special racks, which shall be placed in a hole created in the floor. Special racks shall have a structure, in which bolts used to fix the devices on the concrete floor are visible.

(f)	Components of the Equipment

The Equipment shall consist of the components and devices in Table 54-5 and Table 54-6.

Table 54-5: Components of FM Radio Rebroadcasting System

| Item | Requirements | Unit | Q’ty |
| --- | --- | --- | --- |
| FM receiving antenna | Yagi-antenna/3EL | unit | 8 |
| FM radio broadcasting equipment |  |  |  |
| FM receiver unit |  | CH | 8 |
| FM broadcast switching unit |  | unit | 2 |
| FM transmitter unit | 3W | CH | 8 |
| FM output mixer unit | 8ch | unit | 1 |
| Fixed attenuator |  | unit | 1 |
| Operation control unit (IP) |  | unit | 1 |
| Voice conversion unit | VoIP (1ch) | unit | 1 |
| Layer 2 Ethernet switch | 8 or more ports | unit | 1 |
| Voice level adjustment unit |  | unit | 1 |
| Voice memory unit |  | unit | 1 |
| Power supply unit |  | unit | 1 |
| Terminal unit |  | unit | 1 |
| Cabinet | W570×H2350×D600 | unit | 1 |
| FM radio rebroadcasting system operation console |  |  |  |
| PC (keyboard/mouse) |  | set | 1 |
| Software |  | set | 1 |
| Display unit |  | unit | 1 |
| Microphone unit |  | unit | 1 |
| Speaker unit |  | unit | 1 |
| Audio amplification unit |  | unit | 1 |
| Voice transmitter unit | VoIP (1ch) | unit | 1 |
| Layer 2 Ethernet switch | 8 or more ports | unit | 1 |
| Desk (OA desk) | Including terminal unit | unit | 1 |
| Spare parts / accessories |  | set | 1 |
| Guide sign board |  | board | 2 |

Table 54-6: Components of Loudspeaker Equipment

| Item | Requirements | Unit | Q’ty |
| --- | --- | --- | --- |
| Loudspeaker equipment |  |  |  |
| Pre-amplifier unit |  | unit | 3 |
| Power amplifier unit #1 | for emergency parking zone (120W) | unit | 1 |
| Power amplifier unit #2 | for evacuation connection tunnel (60W) | unit | 1 |
| Power amplifier unit #3 | for tunnel entrance (60W) | unit | 1 |
| Monitor panel unit |  | unit | 1 |
| Power supply unit |  | unit | 1 |
| Terminal unit |  | unit | 1 |
| Cabinet | W570×H2350×D600 | unit | 1 |
| Loudspeaker for tunnel entrance | 25W | unit | 2 |
| Loudspeaker for emergency parking zone | 15W | unit | 6 |
| Loudspeaker for evacuation connection tunnel | 5W | unit | 7 |
| Microphone box |  | unit | 8 |

(g)	Specifications of Components (FM Radio Rebroadcasting System)

Components of the Equipment shall conform with the following specifications:

(i)	FM receiving antenna

Structures, etc.

FM receiving antenna shall have the following specifications:

- Type:  Yagi three-element antenna

- Structure:  support-mounted, waterproof

- Connection:  N connector

- Survival wind speed:  Maximum instantaneous wind speed: 60m/s (when mounted to support)

Electrical specifications

- Received frequency:

CH1,   91.2MHz

CH2,   95.6MHz

CH3,   96.1MHz

CH4,   99.4MHz

CH5,   104.2MHz

CH6,   105.4MHz

CH7,   106.3MHz

CH8,   106.7MHz

- Directional characteristics:  unidirectional

- Gain:  5.5dBi or higher

- Characteristic impedance:  50Ω, unbalanced

(ii)	(FM radio broadcasting equipment

FM receiver unit

- Received frequency:

CH1,   91.2MHz

CH2,   95.6MHz

CH3,   96.1MHz

CH4,   99.4MHz

CH5,   104.2MHz

CH6,   105.4MHz

CH7,   106.3MHz

CH8,   106.7MHz

- Input impedance:  50Ω

- Input level:  40 to 90dBμV (standard level: 60dBμV)

- Output impedance:  600Ω, balanced

- Output level:  0dBm

- No. of channels:  8 channels

FM broadcast switching unit

- Input frequency:  10.7MHz

- Input/output impedance:  600Ω, balanced

- Input level:  to be matched with FM receiver unit

- Output level:  to be matched with FM transmitter unit

- No. of switchable inputs:  7 inputs

- No. of switchable outputs:  10 outputs

FM transmitter unit

- Transmit frequency:

CH1,   91.2MHz

CH2,   95.6MHz

CH3,   96.1MHz

CH4,   99.4MHz

CH5,   104.2MHz

CH6,   105.4MHz

CH7,   106.3MHz

CH8,   106.7MHz

- Input impedance:  600Ω, balanced

- Input level:  0dBm

- Output impedance:  50Ω, unbalanced

- Transmission output:  Rated 3W/ch

- Spurious:  at least -40db below the fundamental emission

- Transmit frequency deviation:	within ±1×10-5

- Alarm display:  output abnormality and power abnormality

- Monitor:  Transmit output display

- No. of channels:  8 channels

- Modulated input frequency band:  200Hz to 7.5kHz

- Maximum frequency deviation:  ±75kHz (100% deviation)

- Pre-emphasis:  50μs or 75μs

- Distortion factor:  1.5% or below (1kHz, 100% deviation)

FM output mixer unit

- Input frequency:  object frequency within the range in 87.5MHz and 108MHz

- Input/output impedance: 50Ω, unbalanced

- Passing power:  Rated 3W/ch

- Passing loss:  10dB/ch or below

- Mixed frequency:  8 waves

Fixed attenuator

- Attenuation:  Selectable from 3dB, 6dB, and 9dB

Operation control unit (IP)

Operation control unit shall control interruptive broadcast from the FM radio rebroadcasting system operation console at the Control Office, and have various monitoring functions.

- The unit shall rebroadcast radio broadcast in normal circumstances, and provide the following interruptive broadcast in emergency.

        - Interruption of radio broadcasting

- Priority order of interruptive broadcast control:

Priority 1: Microphone box

Priority 2: Microphone unit on cabinet rack

Priority 3: FM radio rebroadcasting system operation console

- Monitoring display function

        - The unit shall monitor audio outputs of transmitter units.

        - The unit shall, through audio output indicator, monitor meters corresponding to a monitor selected.

        - The unit shall display whereabouts of defects in case of abnormality with transmit outputs or any device including breakage of guide wires.

- Display language:  English

- Conditions of interface with the FM radio rebroadcasting system

        - Items to be delivered shall be according to Table 54-7.

Table 54-7: Items Monitored/Controlled by FM Radio Rebroadcasting System

| No. | Items monitored/controlled | Control | Monitoring |
| --- | --- | --- | --- |
| 1 | Radio broadcasting, interruptive | ○ | ○ |
| 2 | Radio broadcasting, interruptive (backup) | ○ | ○ |
| 3 | Broadcasting from loudspeaker for emergency parking zone | ○ | ○ |
| 4 | Broadcasting from loudspeaker for emergency parking zone (backup) | ○ | ○ |
| 5 | Broadcasting from loudspeaker for tunnel entrance | ○ | ○ |
| 6 | Broadcasting from loudspeaker for tunnel entrance (backup) | ○ | ○ |
| 7 | Broadcasting from loudspeaker for evacuation connection tunnel | ○ | ○ |
| 8 | Broadcasting from loudspeaker for evacuation connection tunnel (backup) | ○ | ○ |
| 9 | Monitor changeover | ○ | ○ |
| 10 | Monitor changeover (backup) | ○ | ○ |
| 11 | Monitoring FM CH1 | ○ | ○ |
| 12 | Monitoring FM CH2 | ○ | ○ |
| 13 | Monitoring FM CH3 | ○ | ○ |
| 14 | Monitoring FM CH4 | ○ | ○ |
| 15 | Monitoring FM CH5 | ○ | ○ |
| 16 | Monitoring FM CH6 | ○ | ○ |
| 17 | Monitoring FM CH7 | ○ | ○ |
| 18 | Monitoring FM CH8 | ○ | ○ |
| 19 | Monitoring loudspeaker for emergency parking zone | ○ | ○ |
| 20 | Monitoring loudspeaker for tunnel entrance | ○ | ○ |
| 21 | Monitoring loudspeaker for evacuation connection tunnel | ○ | ○ |
| 22 | Microphone unit on cabinet rack in use |  | ○ |
| 23 | Microphone box in use |  | ○ |
| 24 | Radio, output abnormality |  | ○ |
| 25 | Radio, output abnormality (backup) |  | ○ |
| 26 | Radio, power abnormality |  | ○ |
| 27 | Radio, power abnormality (backup) |  | ○ |
| 28 | Loudspeaker, output abnormality |  | ○ |
| 29 | Loudspeaker, output abnormality (backup) |  | ○ |
| 30 | Loudspeaker, power abnormality |  | ○ |
| 31 | Loudspeaker, power abnormality (backup) |  | ○ |

Voice conversion unit

Voice conversion unit shall convert voice-band signals to digital data, and transmit it to LAN. Conversely, it shall also convert voice data received from LAN to voice-band signals.

- Usage:  Voice interruption and signal monitoring

- Line interface: 4-line

        - Interface: 10BASE-T/100BASE-TX (auto-negotiation)

        - Physical specification: RJ-45

- Frequency band: ±3dB in the range of 200Hz and 22kHz (standard of 1kHz)

- Voice input unit:

        - No. of inputs: 2 channels/unit

        - Input impedance: 600Ω

        - Input level:  -10dBm (rated)

- Voice output unit:

        - No. of outputs: 2 channels/unit

        - Output impedance: 600Ω

        - Output level: -10dBm (rated)

Layer 2 Ethernet switch

- Compliance standards: IEEE802.3 (10BASE-T)

- IEEE802.3u (100BASE-TX)

- Interface for devices:

- Interface: 10/100BASE-TX

- Cable:  UTP cable (Category 5 or higher)

- Connector:  RJ-45

- Port:  8 or more ports

Voice level adjustment unit

Voice level adjustment unit shall have a function of fine-tuning the voice level.

- Line input: -10dBm to 0dBm (standard of 1kHz)

- Signal/noise ratio:  50dB or higher

- Distortion factor:  3% or below (1kHz)

Voice memory unit

Voice memory unit shall play interruptive broadcast and voice from loudspeaker. It shall also play voice recorded in a digital storage medium.

- Playback frequency band:  ±3dB in the range of 200Hz and 22kHz (standard of 1kHz)

- Output level:  -10dBm (rated)

- Playback time:  30 secs/set of sentences

- Broadcasting announcement:  8 sets of sentences

Power supply unit

- Single-phase AC two-line:	AC100V±10%, 50Hz/60Hz

- Power consumption: 1600VA or below

Terminal unit

Terminal unit shall connect various units. It shall also have connection terminals with external devices.

Cabinet

- Structure:	Indoor rack

Stand-alone, steel

- External dimensions:	Width: 570mm

Height: 2350mm

Depth: 600mm

(except protruding parts)

(iii)	FM radio rebroadcasting system operation console

FM radio rebroadcasting system operation console shall provide interruptive broadcast to the tunnel wen radio rebroadcasting is in service. It shall also display the operational status of broadcasting equipment. Emergency broadcasting command console shall provide interruptive broadcast to radio rebroadcasting. The basic functions are as follows.

The operation console shall be equipped with the functions of a server, if necessary.

PC (keyboard/mouse), software, display unit, microphone unit, and speaker unit

- Functions and electrical characteristics

        - CPU:  operating frequency of 1.6GHz or more

        - Main memory:  2GB or more

        - Hard disk: 320GB or more

        - Network: IEEE802.3 10/100BASE-TX compatible

        - Sound: Line input, line output, microphone input

        - Display: 17-inch LCD or equivalent

        - Input device: Keyboard

        - Pointing device: Two-button mouse or equivalent

        - Microphone: Upright microphone

        - Speaker: Stereo speaker for PC (with volume)

        - Power: AC100V 50Hz/60Hz

        - OS: Windows OS

- Display and operations

        - Selection and display of broadcasting site

Select Name:	Nagdhunga Tunnel

        - Changeover of sound source

Microphone

Fixed phrases in the voice memory unit

        - Changeover and display of broadcasting monitor

Display unit shall enable to monitor radio broadcast. It shall enable to monitor and display screens and channels selected.

        - Items monitored and displayed

Items to be monitored and displayed shall be according to Table 54-7: “Items Monitored/Controlled by FM Radio Rebroadcasting System”.

The console shall give alarm (buzzer, etc.) when any of the following abnormalities is displayed.

・ Radio, output abnormality

・ Radio, power abnormality

・ Loudspeaker, output abnormality

・ Loudspeaker, power abnormality

        - History

The operation console shall store and display history of signal information about interlocking broadcasts provided.

The history screen shall consist of a facility history screen displaying items monitored by the broadcasting equipment, and a broadcast history screen displaying phrases and announcements made in the past.

        - Display language:  English

- Communication processing for integrated management server:

The operation console shall communicate with the integrated management server to transmit and receive the following signals.

        - Communication protocol:  TCP/IP

        - Target tunnel:  Nagdhunga Tunnel

        - Receiving information:  Emergency information in the tunnel

        - Transmitting information:  Information about defects of FM radio rebroadcasting system

- Interlocking broadcast processing

The operation console shall automatically or semi-automatically process interlocking broadcast when receiving emergency information.

        - Automatic mode:  The operation console shall automatically play interruptive broadcast to the tunnel in response to emergency signals.

        - Semi-automatic mode:  When receiving emergency information, the operation console shall enable operators to play interruptive broadcast after taking confirmation procedures.

Audio amplification unit

Audio amplification unit shall compensate for audio signal characteristics transmitted from the FM radio rebroadcasting system operation console, and transmit monitor audio signals.

- Microphone input:  1 system (600Ω, unbalanced)

- Line input:  -20dBm to 0dBm (standard of 1kHz)

- Line output:  0dBm

- Speaker output:  1 system

- Monitor:  Audio line level display

Voice conversion unit

Voice conversion unit shall convert voice-band signals to digital data, and transmit it to LAN. Conversely, it shall also convert voice data received from LAN to voice-band signals.

- Usage:  Voice interruption and signal monitoring

- Line interface:  4-line

- Interface:  10BASE-T/100BASE-TX (auto-negotiation)

- Physical specification:  RJ-45

- Frequency band:  ±3dB in the range of 200Hz and 22kHz (standard of 1kHz)

- Voice input unit:

        - No. of inputs:  2 channels/unit

        - Input impedance:  600Ω

        - Input level:  -10dBm (rated)

- Voice output unit:

        - No. of outputs:  2 channels/unit

        - Output impedance:  600Ω

        - Output level:  -10dBm (rated)

4)	Layer 2 Ethernet switch

- Compliance standards:

        - IEEE802.3 (10BASE-T)

        - IEEE802.3u (100BASE-TX)

- Interface for devices:

        - Interface:  10/100BASE-TX

        - Cable:  UTP cable (Category 5 or higher)

        - Connector:  RJ-45

        - Port:	8 or more ports

Desk (OA desk)

- Type:  General-purpose product (OA desk)

- External dimensions:  approx. W1200mm×H700mm×D1150mm; (except protruding parts)

- Color:  To be instructed

- Others: Device rack inclusive

(iv)	Spare parts and accessories

The following spare parts and accessories shall be supplied:

Lamp and fuse:  100% of items currently used

Relay:  One each of the types used

Test cable:  One each of the types used

The following documents shall be attached to the System:

Test report:  1 copy

User’s manual:  1 copy

(v)	Guide sign board

Guide sign boards shall be placed on the walls of both sides of the tunnel entrance to inform that radio rebroadcasting service is in progress inside the tunnel. Other specifications shall be according to design drawings.

Guide display method:  Reflective

Material:  Aluminum alloy

Display surface:  Reflective sheet of capsule-lens type

Contents:  Guide on “FM Radio”

Size:  See the drawing

Quantity:  2 boards

(h)	Specifications of Components (Loudspeaker Equipment)

Components of loudspeaker equipment shall conform with the following specifications:

(i)	Loudspeaker equipment

Pre-amplifier unit

- Voice input:  -10 to 0dBm, 600Ω, balanced

- Voice output:  0dBm, 600Ω, balanced

- Frequency characteristics:  60 to 7,000Hz, within ±3dB

- Signal/noise ratio:  60dB or higher

- Distortion factor:  3% or below (1kHz)

- Parametric equalizer:

        - Correction frequency range:  3 frequencies to be selected from the 1/3 octave band width in the range between 20 and 20,000Hz

        - Correction level:  ±12dB

Power amplifier unit #1 (for emergency parking zone)

- Voice input:  0dBm, 600Ω / high impedance switchable, balanced

- Voice output:  120W

- Load impedance:  100V, load line

- Frequency characteristics:  50 to 7,000Hz, within ±3dB

- Signal/noise ratio:  65dB or higher

- Distortion factor:  3% or below (1kHz)

Power amplifier unit #2 (for evacuation connection tunnel)

- Voice input:  0dBm, 600Ω / high impedance switchable, balanced

- Voice output:  60W

- Load impedance:  100V, load line

- Frequency characteristics:  50 to 7,000Hz, within ±3dB

- Signal/noise ratio:  65dB or higher

- Distortion factor:  3% or below (1kHz)

Power amplifier unit #3 (for tunnel entrance)

- Voice input:  0dBm, 600Ω / high impedance switchable, balanced

- Voice output:  60W

- Load impedance:  100V, load line

- Frequency characteristics:  50 to 7,000Hz, within ±3dB

- Signal/noise ratio:  65dB or higher

- Distortion factor:  3% or below (1kHz)

Monitor panel unit

- Monitor panel:  capable of monitoring each speaker line system, up to 6 systems

- Speaker:  0.5W (rated)

Power supply unit

- Single-phase AC two-line: AC100V±10%, 50Hz/60Hz

- Power consumption:  2000VA or below

Terminal unit

Terminal unit shall connect various units. It shall also have connection terminals with external devices.

Cabinet

- Structure:  Indoor rack

Stand-along, steel

- External dimensions:

Width: 570mm

Height: 2350mm

Depth: 600mm

(except protruding parts)

(ii)	Loudspeaker for tunnel entrance

Type: Horn speaker

Playback frequency band:	400Hz to 5,000Hz (at least 20db below output sound pressure level)

Rated input: 25W

Sound pressure level: 110dB or higher (at 1W/1m)

Rated impedance: 400Ω

(iii)	Loudspeaker for emergency parking zone

Type:  Horn speaker

Playback frequency band: 400Hz to 5,000Hz (at least 20db below output sound pressure level)

Rated input: 15W

Sound pressure level: 106dB or higher (at 1W/1m)

Rated impedance: 670Ω

(iv)	Loudspeaker for evacuation connection tunnel

Type: Horn speaker

Playback frequency band:	400Hz to 5,000Hz (at least 20db below output sound pressure level)

Rated input:  5W

Sound pressure level:  104dB or higher (at 1W/1m)

Rated impedance:  2000Ω

(v)	Microphone box

Microphone box shall be installed inside the tunnel, and have a function of simultaneously delivering announcement from the embedded microphone to all the broadcasting systems.

Overview

Microphone box shall be steel-made, electrically and mechanically durable, and dust- and rainproof. It shall be mountable to the tunnel entrance and emergency parking zone.

External dimensions

The standard dimensions are as follows:

- External dimensions:

Width: 250mm

Height: 250mm

Depth: 150mm

(except protruding parts)

Painting color: Munsell N5, gloss

Electrical specifications:

- Power system:  Supply voltage + 24V ±10％ (to be supplied by the loudspeaker equipment)

- Microphone : Close-talking hand microphone (with press talk switch)

- Frequency characteristics:  300Hz to 3.4kHz, within ±15dB

- Output level:  0dBm, 600Ω, balanced

- Load current:  65mA or below

- Others: Microphone box shall have indicators showing that signals from the microphone are being transmitted, and that the microphone is in use.

(5)	VHF Radio Auxiliary Equipment (Including VHF Radio For Road Administrator)

(a)	Application

This section shall apply to components, etc. of the VHF radio auxiliary equipment to be installed in the Nagdhunga Tunnel (hereinafter referred to as the “Equipment”).

(b)	System Overview

The system overview of the Equipment shall be as follows.

(i)	VHF radio for road administrator

VHF Radio for road administrator shall consist of base station, mobile station (portable radio), and operating console.

(ii)	VHF radio auxiliary equipment

VHF radio auxiliary equipment shall be used for communications in and outside the road tunnel to secure smooth maintenance and administrative duties in normal circumstances, and emergency transmission of various information in emergency.

VHF radio for administrator:  The Equipment shall use leaky coaxial cables (LCX), which shall be also for FM radio facilities, to enable radio communications between the fixed radio in the Electric Room (bandwidth of 150MHz) and VHF radios for administrators inside the Nagdhunga Tunnel and both entrances.

Firefighting radio:  The Equipment shall use leaky coaxial cables (LCX) to communicate with firefighting radio (bandwidth of 150MHz) in the tunnel, which shall be connected to the connection terminal box installed at the entrance.

Police radio:  The Equipment shall use leaky coaxial cables (LCX) to communicate with police radio (bandwidth of 150MHz) in the tunnel, which shall be connected to the connection terminal box installed at the entrance.

(c)		Service Space

(i)	VHF Radio for road administrator

Base station and operating console shall be designed for indoor use, and mobile station (portable radio) for outdoor use.

(ii)	VHF radio auxiliary equipment

Connection terminal box, and duplexer and terminator shall be designed for outdoor use, and duplexer for indoor use.

(d)		Ambient Conditions

Temperature:

- Outdoor and inside the tunnel, -15°C to 50°C

- Indoor, 0°C to 40°C

- However, 10°C to 35°C for general information devices

Humidity:

- relative humidity of 85%RH or below

- However, 20 to 80%RH (non-condensing humidity) for general information equipment

Wind speed:	Maximum instantaneous wind speed: 60m/s (for outdoor devices only)

(e)	Structures

Individual server equipment and racks shall have the following structures.

The Equipment shall be made of durable and rust preventive steel.

Stand-along devices shall be earthquake-resistant to prevent accidents due to horizontal displacement, falling or drop of any parts.

Devices shall be mounted on steel racks, which shall be fixed directly and horizontally on concrete floors.

Devices to be placed on the free access floor shall be fixed with bolts on special racks, which shall be placed in a hole created in the floor. Special racks shall have a structure, in which bolts used to fix the devices on the concrete floor are visible.

(f)	Components of the Equipment

The Equipment shall consist of the following components and devices.

Table 54-8: Components of VHF Radio Auxiliary Equipment

| Name | Specifications | Unit | Q’ty |
| --- | --- | --- | --- |
| VHF Radio for road administrator |  | set | 1 |
| Operating console |  | set | 1 |
| Base station |  | set | 1 |
| Base station antenna | Yagi three-element antenna | unit | 2 |
| Distributor | Two-distributor (1:9) | unit | 1 |
| Portable radio |  | unit | 12 |
| Duplexer |  | unit | 1 |
| Duplexer and terminator |  | unit | 1 |
| Connection terminal box (for police radio) |  | unit | 2 |
| Connection terminal box (for firefighting radio) |  | unit | 2 |
| Leaky Coaxial cable | L-LCX-43D-65-HR | m | 1500 |
| Leaky Coaxial cable | L-LCX-43D-55-HR | m | 1168 |

(g)	Specifications of Components (VHF Radio for road administrator)

(i)	System functions

Group talk: The Equipment shall have a group talk function for point-to-multipoint communication, which provides information from a single user to multiple users with portable radios in the same group.

Concurrent talk (all group talk):  The Equipment shall have a concurrent talk function for broadcast communication, a special type of group talk, which provides information to all radios under the system or mobile stations in a specific area.

Direct talk between mobile stations:  The Equipment shall have a function to enable multiple mobile stations to communicate directly with each other, rather than via the base station.

Voice and data security:  The Equipment shall have a scramble function to make digital voice and data unintelligible at unidentified receivers.

Text message transmission: The Equipment shall have a function to send fixed-phrase and free-text messages in individual address communications between the command console and mobile stations.

- Fixed-phrase message: up to 12 characters

- Free-text message: up to 50 characters from the console

(ii)	Operating console

Operating console shall be used for voice calls and text messages, and have the following functions.

Functions

- Group talk/concurrent talk

- Text message

        - Fixed-phrase message:  up to 12 characters

        - Free-text message:  up to 50 characters from the console

- Monitoring

        - Operating console shall monitor alarms and status of the base station.

Specifications

- OS: Windows (64bit) or equivalent

- Operating environment:  24-hour continuous operation

- Display language:  English

- Sound:  Line input, line output, microphone input

- Display:  17-inch LCD or equivalent

(iii)	Base station

Functions

- Redundancy:  Base station shall have redundant structures. It shall consist of components for use and backup, and have the following redundant units.

        - Radio units

        - Power units

When detecting alarm signals, Base station shall automatically switch from the units in use to backup units.

- Stand-alone

Base station shall be operable in the stand-alone mode when detecting network failure.

Specifications

- Radio frequency bandwidth:  band of 150MHz

- Frequency:  146 to 162MHz

- Frequency spacing: 6.25kHz

- Antenna power:  Range of 1 to 20W

- Modulation:  4FSK modulation type

- Access: SCPC

- Communication: half-duplex with 2 frequencies

- Transmission speed: 4.8kbps

- Voice encoding speed: 3.6kbps (including error-correction code)

- Voice encoding method: AMBE+2 enhanced half-rate

- Frame length: 80ms

- Transmission/reception performance: in compliance with the following “Requirements for transmitter/receiver”

- Power unit:	Single-phase AC two-line:  AC100V, 50Hz/60Hz

External output

Base station shall output monitoring signals about the state of devices to PLC of the monitoring control equipment.

Interface for PLC shall be non-voltage continuous contact signals.

(iv)	Requirements for Transmitter/Receiver

Transmitter

- Allowable deviation from the frequency: Transmitter shall satisfy the following allowable deviations from the specified frequency.

Table 54-9: Allowable Deviation from Frequency

(unit: ppm)

| 150MHz bandwidth | Base station | ±2.5 |
| --- | --- | --- |
|  | Mobile station | ±2.5 |

- Allowable spurious or unwanted emission levels: The values shall comply with the following table.

Table 54-10: Allowable Spurious or Unwanted Emission Levels

| Antenna power | Allowable out-of-band spurious emission level | Allowable spurious-band unwanted emission level |
| --- | --- | --- |
| More than 1W but 50W or lower | 2.5μW or lower, or 60db lower than the average power at the basic frequency | 2.5μW or lower, or 60dB lower than the carrier power at the basic frequency |
| 1W or lower | 2.5μW or lower | 2.5μW or lower |

- Allowable occupied bandwidth: Allowable occupied bandwidth shall be 5.8kHz or lower

- Allowable antenna power deviation: Allowable antenna power deviation shall be 20% above the upper limit and 50% below the lower limit.

- Adjacent channel leakage power:

The amount of power in the band of ±2kHz from the frequency 6.25kHz away from the designated carrier frequency shall be as follows:

When the transmission output is 1W or below, the ACLP shall be lower than -45db then transmission power. When the output exceeds 1W, the ACLP shall be -55dB or lower or 32μW or lower.

Standard values of the adjacent channel power ratio (ACPR) and adjacent channel leakage power (ACLP) shall be in accordance with the details shown in Figure 54-1:

Figure 54-1: Standard Values of Adjacent Channel Power Ratio (ACPR) and Adjacent Channel Leakage Power (ACLP)

- Body radiation: Body radiation shall be 2.5μW or below

- Allowable deviation of transmission speed: Allowable deviation of transmission speed shall be within ±5.0×10-6

- Frequency deflection:  When a code string of “+3, +3, -3, -3, +3, +3, -3, -3” is repeatedly input as modulated signals, the frequency deflection shall fall under the range of 1083Hz and 1324Hz. The standard frequency deviation for the code string shall be ±1203Hz (4 / π×945 = ±1203Hz, based on the frequency deviation of ±945Hz corresponding to symbol ±3), and shall not be deviated by ±10% from the standard value.

- Modulation accuracy: The modulation accuracy (FSK error) shall be 5% or below. FSK error is defined as the root mean squared (r.m.s) in percentage of the frequency shift at symbol locations.

Receiver

- Frequency variation of local oscillator: Specific regulations shall not be defined for the frequency variation of local oscillator.

- Receiving sensitivity: When signals modulated with two pseudo-noise (PN) codes of bit period of 511 code length are bit transmitted, and the bit error rate (BER) for static and fading channels are 1×10-2 and 3×10-2, respectively, the receiving input level shall take the value provided in Table 54-11.

Specific regulations shall not be defined for diversity receiving characteristics.

Table 54-11: Receiving Sensitivity

| BER | 1×10-2 (static) | 3×10-2 (fading) |
| --- | --- | --- |
| Receiving input level | 0 dBμV (standard sensitivity) or lower | 5.0 dBμV or lower (Non-diversity) |

Fading condition: Rayleigh fading with the maximum Doppler frequency of 7.5Hz at 150MHz band

- Spurious response: Together with the desired wave with the standard sensitivity of 3dB, when the bit error rate is 1×10-2 because of non-modulated interfering wave detuned from the desired wave by 12.5kHz or more, the ratio of the interfering wave and desired wave levels shall be 53dB or higher.

- Adjacent channel selectivity: Together with the desired wave with the standard sensitivity of 3dB, when the bid error rate is 1×10-2 because of interfering wave modulated by digital signals detuned by 6.25kHz (two pseudo-noise codes of bit period of 32,767 code length), the ratio of the interfering wave and desired wave levels shall be 42dB or higher.

- Intermodulation characteristic: Together with the desired wave with the standard sensitivity of 3dB, the bid error rate is 1×10-2 because of two non-modulated interfering waves detuned from the desired wave by 12.5kHz and 25kHz, respectively, the ratio of the interfering wave and desired wave levels shall be 53dB or higher.

- Strength of secondary radiated emissions: The strength of secondary radiated emissions shall be 4nW or below.

- Body radiation: Body radiation shall be 4nW or below at 1GHz or below, and 20nW or below at the range between 1 and 3GHz.

(v)	Base station antenna

Type:  Yagi three-element antenna

Structure:  Pole-mounted, waterproof

Connection:	N connector

Survival wind speed:  Maximum instantaneous wind speed: 60m/s

- (when mounted to pole)

Frequency:  Specific frequency

Gain:  8dBi or higher

Characteristic impedance:  50Ω, unbalanced

(vi)	Distributor

Type:  150MHz bandwidth, two-distributor

Distribution ratio:  1:9

Input/output impedance:  50Ω

Input/output connector:  N connector

(vii)	Portable radio

Operational functions

- Portable radio shall have a function of switching communication channels.

- Portable radio shall have a function of switching communication modes (concurrent talk, group talk and direct talk between mobile stations).

- Portable radio shall have a volume adjustment function.

- Portable radio shall have a function of power cutoff.

- Portable radio shall have a function of disabling key operations (key lock) to prevent incorrect operations. It shall, however, transmit and receive communications even when locked.

Display functions

- Portable radio shall display the status of direct talks between mobile stations.

- Portable radio shall display the status of communication modes (concurrent talk, group talk and direct talk between mobile stations).

- Portable radio shall have an indicator showing that transmission is in progress.

- Portable radio shall identify the electric field strength of radio waves received.

- The display unit shall have a backlight.

- Portable radio shall display the status of power on/off.

Maintenance functions

Portable radio shall have the following maintenance functions.

- Measuring transmission output levels

- Transmitting test patterns for measuring BER

- Preventing incorrect use

- Having an earphone jack

Specifications

- Radio frequency bandwidth:  band of 150MHz

- Frequency:  146 to 162MHz

- Frequency spacing:  6.25kHz

- Antenna power:  Range of 1 to 5W

- Modulation:  4FSK modulation type

- Access:  SCPC

- Communication:  half-duplex with 2 frequencies or with 1 frequency

- Transmission speed:  4.8kbps

- Voice encoding speed:  3.6kbps (including error-correction code)

- Voice encoding method:  AMBE+2 enhanced half-rate

- Frame length:  80ms

- Transmission/reception performance:  Same as VHF radio base station

- Dust- and waterproof:  JIS C 0920 IP57 or higher

- External dimensions:  Approx. W62.5×H97.5×D30mm

(except protruding parts) (Excluding battery and antenna)

- Weight:  Approx. 120g (excluding battery and antenna)

- Serviceable time:  Approx. 8 hours

(when continuously used of 5% for transmission, 5% of reception and 90% of stand-by)

(h)	Specifications of Components (VHF radio auxiliary equipment)

Components of the VHF radio auxiliary equipment shall conform with the following specifications:

(i)	Duplexer

Duplexer shall be installed in the Electric Room and use leaky coaxial cables (LCX), together with other equipment. The specifications are as follows.

Structures

- Cabinet shall conform with the following specifications:

- Type:  Stand-alone, steel

- External dimensions:

        - Width:  570mm

        - Height:  2350mm

        - Depth:  600mm

- Painting color:  Munsell 5Y7/1, semi-gloss (approx.)

Standards

- Allowable input:  10W/wave

- Frequency bandwidth:  band of 80 to 150MHz

- Impedance:  50Ω, unbalanced

- Matching:  VSWR 1.5 or below

Duplex frequency

- Frequency for administrator:  band of 150MHz

- Frequency for police radio:  band of 150MHz

- Frequency for firefighting radio:  band of 150MHz

- Frequency for FM:  band of 80MHz

Performance

- Insertion loss:

        - 5dB or below at band of 150MHz

        - 1.5dB or below at band of 80MHz

- -50dB or below with leakage between terminals or at frequencies of channels for other organizations

- VSWR:  1.5 or below

- Rated power:  10W / channel

(ii)	Duplexer and terminator

Duplexer and terminator shall be installed at the entrance of the tunnel to enable different equipment to use leaky coaxial cables (LCX). The specifications are as follows.

Structures

- Type:  Stand-alone, steel-made, outdoor use (IP44)

- External dimensions:

        - Width: 760mm

        - Height: 940mm

        - Depth: 580mm

- Processing:	Main body:

        - SUS304

        - Stand: hot-dip galvanizing

- Painting color:	Munsell 10YR2/1, semi-gloss (approx.)

Standards

- Allowable input:  10W

- Frequency bandwidth:  band of 80 to 150MHz

- Impedance:  50Ω, unbalanced

- Matching:  VSWR 1.2 or below

Passing frequency

- Frequency for police radio:  band of 150MHz

- Frequency for firefighting radio:  band of 150MHz

- Frequency for administrator:  band of 150MHz

Terminal frequency

- Frequency for FM:  band of 80MHz

Performance

- Insertion loss:  5dB or below at band of 150MHz

- leakage between terminals:  -50dB or below at frequencies of channels for other organizations

- VSWR: 1.2 or below

- Rated power:  10W

(iii)	Connection terminal box

Connection terminal box shall be installed at the entrance of the tunnel, and connected to firefighting and police radios to enable these radios to use leaky coaxial cables (LCX). The specifications are as follows.

Structures

- Type:  Stand-alone, steel, outdoor (IP44)

- External dimensions:

        - Width: 400mm

        - Height: 1300mm

        - Depth: 430mm

- Processing:	Main body:

        - SUS304

        - Support unit: hot-dip galvanizing

- Painting color:  Munsell 10YR2/1, semi-gloss (approx.)

Standards

- Connector with radio:  N connector x 1 unit

- Accessories:

        - Terminating register: 50Ω/1W

        - N connector structure:  1 unit

        - Coaxial cable:  5D-2V × 10m

        - Double-ended N-P connector:  1 unit

        - Conversion connector:   N-J/BNC-P x 1 unit

(iv)	Leaky coaxial cables (LCX)

Structures

- Internal conductor:	material: copper pipe

- Insulator:	Ladder-line polyethylene (spiral winding), polyethylene pipe and heat-resistant tape

- External conductor:	Aluminum longitudinally supporting tape (with leaky slot)

Horizontally wrapped with plastic tape

- Common coating:	Cables and supporting wires are placed in parallel and coated with heat- and flame resistant black polyethylene

- Outer diameter:

        - A: approx. 68mm

        - B: approx. 51mm

        - C: approx. 13mm

        - D: approx. 4mm

- Others:	Heat-resistant

Standards

- Useful frequency:

        - band of 80MHz, 87 to 107MHz

        - band of 150MHz, 137 to 170MHz

- Standard attenuation:

band of 80MHz:

        - L-LCX-43D-65-HR, 8.0 to 9.5dB/km

        - L-LCX-43D-55-HR, 8.5 to 10dB/km

band of 150MHz:

        - L-LCX-43D-65-HR, 11dB/km

        - L-LCX-43D-55-HR, 12dB/km

- Standard coupling loss:

band of 80MHz:

        - L-LCX-43D-65-HR, 73dB

        - L-LCX-43D-55-HR, 63dB

band of 150MHz:

        - L-LCX-43D-65-HR, 70dB

        - L-LCX-43D-55-HR, 60dB

Where:

L	- LCX	- □D	- □	- HR

*1	*2	*3	*4	*5

*1: L: Low loss type or N/A: general type

*2: LCX: Leaky Coaxial Cable

*3: Outer diameter of insulator e.g. 43D: 43mm

*4: D: Characteristic impedance, e.g. 50Ω

*5: HR: Heat-Resistant or N/A: general type

(6)	CCTV CAMERA EQUIPMENT

(a)	Application

This section shall apply to components, etc. of the CCTV camera equipment to be installed in the Nagdhunga Tunnel (hereinafter referred to as the “Equipment”).

(b)	System Overview

The system overview of the Equipment shall be as follows:

CCTV shall be installed outside the tunnel to monitor vehicles passing through the tunnel and tollgate.

CCTV shall be installed inside the tunnel to monitor emergency exits and evacuation routes.

CCTV shall be installed inside the tunnel to monitor vehicles passing through, emergency exits, emergency parking zone and other fixed points. When an accident or disaster occurs, CCTV shall monitor firefighting and evacuation activities, and the state of the accident or disaster.

The Equipment shall collectively record and deliver video images from all the cameras.

(c)	Service Space

CCTV for outside and inside the tunnel, and control panels shall be designed for outdoor use, and other components for indoor use.

(d)	Ambient Conditions

Temperature:

- outdoor and inside the tunnel, -10°C to 40°C

- Indoor, 0°C to 40°C

However, 10°C to 35°C for general information devices

Humidity:

- outdoor and inside the tunnel, 10% to 90%RH

- indoor, 10% to 85%RH

However, 20 to 80%RH (non-condensing humidity) for general information devices

Wind speed:	Maximum instantaneous wind speed: 60m/s (non-destructive)

- (for outdoor devices only)

(e)	Structures

Individual server equipment and racks shall have the following structures.

The Equipment shall be made of durable and rust preventive steel.

Stand-along devices shall be earthquake-resistant to prevent accidents due to horizontal displacement, falling or drop of any parts.

Devices shall be mounted on steel racks, which shall be fixed directly and horizontally on concrete floors.

Devices to be placed on the free access floor shall be fixed with bolts on special racks, which shall be placed in a hole created in the floor. Special racks shall have a structure, in which bolts used to fix the devices on the concrete floor are visible.

(f)	Components of the Equipment

The Equipment shall consist of the components and devices shown in Table 54-12.

Table 54-12: Components of CCTV Camera Equipment

| Item | Requirements | Unit | Q’ty |
| --- | --- | --- | --- |
| CCTV for outside tunnel (PTZ) |  | unit | 4 |
| CCTV for inside tunnel (PTZ) |  | unit | 4 |
| CCTV for inside tunnel (Fixed) |  | unit | 9 |
| CCTV control panel #1 | for CCTV for outside tunnel (PTZ) | unit | 4 |
| CCTV control panel #2 | for CCTV for inside tunnel (PTZ) | unit | 4 |
| CCTV control panel #3 | for CCTV for inside tunnel (Fixed) | unit | 9 |
| CCTV control equipment |  |  |  |
| Video storage server |  | unit | 1 |
| Media converter |  | unit | 17 |
| Layer 2 Ethernet switch | 24 or more ports | unit | 1 |
| Server rack | W700×H2000×D1000 | unit | 1 |
| Optical terminal box | W700×H2000×D500 | unit | 1 |
| Operation terminal for CCTV |  | unit | 1 |

(g)	Specifications of Components

Components of the Equipment shall conform with the following specifications:

(i)	CCTV for outside tunnel (PTZ)

CCTV shall be installed outside the tunnel to monitor vehicles passing through the tunnel and tollgate.

Functions

- CCTV shall have infrared LED (adjustable floodlight of 30 levels) that enables to see 300m ahead of the camera at night.

- CCTV shall, when infrared LED is on, automatically enter the night mode (black/white) and follow lights.

- The minimum object illuminance shall be 0.0001lx (when the electronic sensitivity function is off (movie), black/white).

- CCTV shall be dust- and waterproof, equivalent to IP66.

- CCTV shall rotate horizontally 360 degrees (when the wind speed is 40m/s).

- CCTV shall output video images equivalent to full HD (1920 x 1080).

Electrical specifications

- Image sensor:  Single CMOS (2/3 inches)

- Maximum resolution:  1920×1080 or higher

- Minimum object illuminance:

        - 0.0001lx or lower (electronic sensitivity is off (movie), black/white).

- Zoom ratio:	 25x or higher optical zoom

- Angle of view: Horizontal, including the range from 51° to 3°

- Illumination: F1.8 or higher

- Focus:  Manual, automatic

- Structure:  JIS C 0920, IP code: IP66 (dust- and waterproof)

- Type:	Stationary

- Rotating angle:

        - Horizontal: 360° endless rotation

        - Vertical: +20° to -70° or more

- Maximum rotating speed:

        - Horizontal: 180°/sec

        - Vertical:   60°/sec

- Positioning accuracy:  ±0.1° or below

- Presetting:  Registration/control of 255 points

- Illumination:

        - Infrared LED x 1

        - Approx. 850mm

        - Adjustable floodlight of 30 levels

- Survival wind speed:  40m/s (manual mode only)

- Dimensions, weight, power consumption:

        - Approx. 750(W)×450(H)×500(D)

        - Approx. 30kg

        - Maximum 400W or below

(ii)	CCTV for inside tunnel (PTZ)

CCTV shall be installed inside the tunnel to monitor emergency exits and evacuation routes.

Functions

- CCTV shall be suspended from the ceiling more than 2.0 to 2.5 meters above the evacuation routes so as not to interfere with evacuation.

- The minimum object illuminance shall be 0.05lx (when the electronic sensitivity function is off (movie), black/white).

- CCTV shall be dust- and waterproof, equivalent to IP66.

- CCTV shall rotate horizontally 360 degrees (when the wind speed is 40m/s).

- CCTV shall output video images equivalent to full HD (1920 x 1080).

Electrical specifications

- Image sensor:  Single CMOS (1/2.8 inches)

- Maximum resolution:  1920×1080 or higher

- Minimum object illuminance:  00.05lx or lower (electronic sensitivity is off (movie), black/white).

- Zoom ratio:	 30x or higher optical zoom

- Angle of view: Horizontal, including the range from 63° to 3°

- Illumination:  F1.6 or higher

- Focus:  Manual, automatic

- Structure:  JIS C 0920, IP code: IP66 (dust- and waterproof)

- Type:  Suspended from the ceiling

- Rotating angle:

        - Horizontal: 360° endless rotation

        - Vertical: +90° to -90°

- Maximum rotating speed:

        - Horizontal: 180°/sec

        - Vertical:   90°/sec

- Positioning accuracy:  ±0.3° or below

- Presetting:	Registration/control of 255 points

- Survival wind speed:  40m/s (manual mode only)

- Dimensions, weight, power consumption:

        - Approx. 300(W)×300(H)×250(D)

        - Approx. 9kg

        - Maximum 90W or below

(iii)	CCTV for inside tunnel (Fixed)

CCTV shall be installed inside the tunnel to monitor vehicles passing through, emergency exits, emergency parking zone and other fixed points. When an accident or disaster occurs, CCTV shall monitor firefighting and evacuation activities, and the state of the accident or disaster.

Functions

- CCTV shall be installed on the side faces of the tunnel. In consideration of the optical angle, and to avoid inferior video images due to reflection of the headlight of vehicles, CCTV shall be installed to see running vehicles from behind. In addition, for easier maintenance and inspection, CCTV shall be placed some 2.5 meters above the road surface.

- CCTV shall be dust- and waterproof, equivalent to IP66.

- CCTV shall be fixed to immediately capture changes in the status (from normal circumstances).

- CCTV shall output video images equivalent to full HD (1920 x 1080).

Electrical specifications

- Image sensor:  Single CMOS (1/2.8 inches)

- Maximum resolution:  1920×1080 or higher

- Minimum object illuminance:  00.05lx or lower (electronic sensitivity is off (movie), black/white).

- Zoom ratio:	 3x or higher optical zoom (preset)

- Angle of view:  Horizontal, 109° to 37° (preset)

- Illumination: F1.2 or higher

- Structure: JIS C 0920, IP code: IP66 (dust- and waterproof)

- Type: Wall-mounted

- Dimensions, weight, power consumption:

        - Approx. 120(W)×220(H)×360(D)

        - Approx. 2kg

        - Maximum 4W

(iv)	CCTV control Panel #1

CCTV control panel shall be placed stand-alone or mounted to a pole near CCTV for outside tunnel (PTZ) to store devices and components to supply power to the camera and accessories, and transmit video images and control signals of the camera. The relevant conductive wires for signal transmission, except for optical fiber cables, shall be connected to protector.

Outdoor case

- Structure:	Stand-alone or pole-mounted

Stainless steel

JIS C 0920, IP code: IP55 (dust- and jet-proof)

- External dimensions:

        - Width: 580mm

        - Height: 650mm

        - Depth: 240mm

(except protruding parts)

Encoder

Encoder shall output digital video images with the resolution of full HD (1920×1080) in IP transmission format (H.264, multicast).

- Input video signal:  Full HD (1920×1080) × 1 channel

- Output signal:  LAN (10/100M Ethernet)

IP transmission format (H.264, multicast)

Media converter

Media converter shall convert signals in LAN cables (copper wire) to signals for optical fiber cables (SM).

- LAN interface: 10/100BASE-TX interface x 1 port

- Optical interface: 100BASE-FX interface x 1 port

        - Interface:  SC connector

        - Transmission distance: within 5km

Optical terminal box

Optical terminal box shall store optical fiber cables with at least eight cores (including backup cables).

- No. of fusion splices:  8 cores or more

- Connector:  SC connector

- No. of adapters:  8 or more

Power supply converter and video protector

Power supply converter shall step down the input voltage, and supply power to the camera and auxiliary equipment. Protector shall be applied to signal and power cables.

- Input voltage:  AC220V±10%

- Output voltage:  AC100V±10%

- Protector:  Protector shall be applied to signal and power cables.

(v)	CCTV control panel #2

CCTV control panel shall be mounted to the wall near CCTV for inside tunnel (PTZ) to store devices and components to supply power to the camera and accessories, and transmit video images and control signals of the camera. The relevant conductive wires for signal transmission, except for optical fiber cables, shall be connected to protector.

Outdoor case

- Structure:

        - Wall-mounted

        - Stainless steel

JIS C 0920, IP code: IP55 (dust- and jet-proof)

- External dimensions:

        - Width: 500mm

        - Height: 800mm

        - Depth: 200mm

(except protruding parts)

Encoder

Encoder shall output digital video images with the resolution of full HD (1920×1080) in IP transmission format (H.264, multicast).

- Input video signal:  Full HD (1920×1080) × 1 channel

- Output signal:  LAN (10/100M Ethernet)

IP transmission format (H.264, multicast)

Media converter

Media converter shall convert signals in LAN cables (copper wire) to signals for optical fiber cables (SM).

- LAN interface: 10/100BASE-TX interface x 1 port

- Optical interface:  100BASE-FX interface x 1 port

        - Interface:  SC connector

        - Transmission distance:  within 5km

Optical terminal box

Optical terminal box shall store optical fiber cables with at least eight cores (including backup cables).

- No. of fusion splices:  8 or more cores

- Connector:  SC connector

- No. of adapters:  8 or more

Power supply converter and video protector

Power supply converter shall step down the input voltage, and supply power to the camera and auxiliary equipment. Protector shall be applied to signal and power cables.

- Input voltage:  AC220V±10%

- Output voltage:  AC100V±10%

- Protector:  Protector shall be applied to signal and power cables.

(vi)	CCTV control panel #3

CCTV control panel shall be mounted to the wall near CCTV for inside tunnel (Fixed) to store devices and components to supply power to the camera and accessories, and transmit video images and control signals of the camera. The relevant conductive wires for signal transmission, except for optical fiber cables, shall be connected to protector.

Outdoor case

- Structure:

        - Wall-mounted

        - Stainless steel

JIS C 0920, IP code: IP55 (dust- and jet-proof)

- External dimensions:

        - Width: 500mm

        - Height: 800mm

        - Depth: 200mm

(except protruding parts)

Encoder

Encoder shall output digital video images with the resolution of full HD (1920×1080) in IP transmission format (H.264, multicast).

- Input video signal:  Full HD (1920×1080) × 1 channel

- Output signal:

        - LAN (10/100M Ethernet)

        - IP transmission format (H.264, multicast)

Media converter

Media converter shall convert signals in LAN cables (copper wire) to signals for optical fiber cables (SM).

- LAN interface:  10/100BASE-TX interface x 1 port

- Optical interface:  100BASE-FX interface x 1 port

        - Interface:  SC connector

        - Transmission distance:  within 5km

Optical terminal box

Optical terminal box shall store optical fiber cables with at least eight cores (including backup cables).

- No. of fusion splices:  8 or more cores

- Connector:  SC connector

- No. of adapters:  8 or more

Power supply converter and video protector

Power supply converter shall step down the input voltage, and supply power to the camera and auxiliary equipment. Protector shall be applied to signal and power cables.

- Input voltage:  AC220V±10%

- Output voltage:  AC100V±10%

- Protector:  Protector shall be applied to signal and power cables.

Power superimposing unit

Power superimposing unit shall superimpose the voltage necessary for operation of video cables of the camera.

(vii)	CCTV control equipment

CCTV control equipment shall collectively record and deliver video images from all the cameras.

Video storage server

- Video storage and operational functions:

Video storage server shall store video image data for maximum two weeks (14 days). Data shall be automatically deleted after a period of two weeks.

It shall enable to view and download video image data recorded and stored from operation terminal for CCTV.

        - Camera view data:  17 camera units or more

        - Data format:  H.264, 1920×1080, 6Mbps

        - Storage period:  17 units x 2 weeks (14 days) or longer

Data shall be automatically deleted after a period of two weeks.

        - Viewing function:  The server shall be able to view and download video image data recorded and stored.

        - Camera control:  The server shall have various functions to control the camera.

- CCTV camera monitoring: Video storage server shall be connected to the CCTV control panels on the network to monitor the state of CCTV camera (the state of video input, delivery, etc.).

- Communication processing for integrated management server: The operation console shall communicate with the integrated management server to transmit and receive the following signals.

        - Communication protocol:  TCP/IP

        - Transmitting information:  Information about the monitoring state of CCTV camera

Media converter

Media converter shall convert signals in LAN cables (copper wire) to signals for optical fiber cables (SM).

- LAN interface:  10/100BASE-TX interface x 1 port

- Optical interface:  100BASE-FX interface x 1 port

Interface:  SC connector

Transmission distance:  within 5km

- Quantity:  17 units

Layer 2 Ethernet switch

- Structure:  Rack-mounted

- Backplane capacity:  100Gbps or more

- No. of interfaces:  10/100/1000BASE-T interface x 24 or more ports

- Compatible standards:

10BASE-T:	IEEE802.3

100BASE-TX:	IEEE802.3u

1000BASE-T:	IEEE802.3ab

- Packet transmission capacity:  maximum 70Mpps or more

- Priority control:  The switch is capable of priority control of traffics in accordance with COS, IP precedence and DSCP value of IEEE802.1p.

- VLAN:

The switch can support 1000 or more functions.

The switch can support VLAN for each port.

It can also configure tag VLAN (IEE802.1Q).

- Fault bypass:  The switch can support independent spanning tree protocol for each VLAN (including tag VLAN).

- Multicast: The switch shall transmit multicast packets only to relevant ports. (Function equivalent to IGMP snooping)

- Management protocol:  SNMP (v1, v2, v3)

- Power:  AC100V 50Hz/60Hz

- Maximum power consumption:  approx. 38W

Server rack

- Structure:

        - Indoor rack

        - Stand-alone, steel

- External dimensions:

        - Width: 700mm

        - Height: 2000mm

        - Depth: 1000mm

(except protruding parts)

(viii)	Optical terminal box

Optical terminal box shall store optical fiber cables from 17 camera units and the West Electric Room.

- No. of fusion splices:  480 or more cores

- Connector:  SC connector

- No. of adapters:  480 or more

- No. of cables contained:

        - 24 or more optical fiber cables

        - 24 or more optical fiber cords

- Server rack

- Structure:

        - Indoor rack

        - Stand-alone, steel

- External dimensions:

        - Width: 700mm

        - Height: 2000mm

        - Depth: 500mm

(except protruding parts)

(ix)	Operation terminal for CCTV

Operation terminal for CCTV shall display camera views, and control the rotation of the cameras. It shall also access to the video storage server to download video image data stored.

Functions:

- Viewing video images of the camera

- Controlling the camera

- Writing data stored in the video storage server

OS:  Windows (64bit) or equivalent

Operating environment:  24-hour continuous operation

Display language:  English

(7)	Test, Installation and Trial Operation

Installation, tests and trial operations of the System shall be conducted in accordance with the relevant drawings. Factory Acceptance Test (FAT) and Site Acceptance Test (SAT) shall be conducted in the following manner to demonstrate that the System performance meets the specifications, equipment manufacturing specifications and other relevant documents.

(a)	Factory Acceptance Test (FAT)

Factory Acceptance Test (FAT) shall be conducted at the manufacturing factory in accordance with the test plan and procedure manual. Upon the completion, the following test reports and documents shall be submitted.

(i)	Test reports chiefly to confirm physical performance

- Test report to confirm the performance of components, materials and parts

- For general equipment and materials including appliance products, test data on their catalogs and manuals

- Test report to confirm the performance of equipment, which consists of multiple components and materials

(ii)	Test reports chiefly to confirm theoretical performance

- Test report to confirm the performance of components and materials, and functions

- Test report to confirm the functions of equipment, which consists of multiple components and materials.

- Test report to confirm the functions of devices that are combined with other devices when used

(b)	Site Acceptance Test (SAT)

Comprehensive test and adjustment shall be conducted on site to check the operation of the entire System.

The Contractor shall create and obtain the approval for a test plan for SAT, and submit the results of the test and adjustment in the form of Site Test Report.

(8)	Spare Parts

To ensure efficient and continuous operations of the System, spare parts shall be supplied for equipment, components and devices, which could adversely affect the system operation or need to be promptly repaired if they suffer from any defect.

Spare parts to be procured as part of the System shall be listed in Table 54-13.

Table 54-13: Spare Parts List

| Item | Requirements | Q’ty | Unit |
| --- | --- | --- | --- |
| VHF radio auxiliary equipment / FM radio rebroadcasting system |  |  |  |
| FM broadcasting equipment |  |  |  |
| FM transmitter unit |  | 1 | unit |
| Voice conversion unit, VoIP |  | 1 | unit |
| Voice memory unit |  | 1 | unit |
| FM receiver unit |  | 1 | unit |
| Loudspeaker equipment |  |  |  |
| Power amplifier unit (120W) |  | 1 | unit |
| Power amplifier unit (60W) |  | 1 | unit |
| Pre-amplifier unit |  | 1 | unit |
| VHF Radio for road administrator |  |  |  |
| Base station (radio unit) |  | 1 | unit |
| Base station (power unit) |  | 1 | unit |
| Portable radio |  | 1 | unit |
| CCTV camera equipment |  |  |  |
| CCTV camera |  |  |  |
| CCTV for outside tunnel (PTZ) |  | 1 | unit |
| CCTV for inside tunnel (PTZ) |  | 1 | unit |
| CCTV for inside tunnel (Fixed) |  | 1 | unit |
| Control panel |  |  |  |
| Encoder | for CCTV control panels #1, #2 and #3 | 2 | unit |
| Protector for power supply | for CCTV control panels #1 and #2 | 1 | unit |
| Protector for controller | for CCTV control panels #1 and #2 | 1 | unit |
| Video protector | for CCTV control panels #1 and #2 | 1 | unit |
| Power superimposing unit | for CCTV control panel #3 | 1 | unit |
| Video protector (power superimposing) | for CCTV control panel #3 | 1 | unit |
| Monitoring control equipment |  |  |  |
| PLC |  |  |  |
| Communication processing unit | PLC, PLC2, software-bundled | 2 | unit |
| Monitoring input unit |  | 2 | unit |
| Measurement input unit |  | 2 | unit |
| Control output unit |  | 2 | unit |
| Relay unit | Relay unit (to replace 1 contact) | 10 | unit |
| Power unit | Power unit (for communication processing unit) | 2 | unit |
| DC power supply | Power unit (for monitoring control unit) | 2 | unit |

5500.	TUNNEL VENTILATION SYSTEM

(1)	General

(a)	Description

These works consist of the Tunnel Ventilation System Dust Countermeasure Plan that shall be installed for the Project and shall be composed of at least the following items:

- Details of ventilation systems during excavation and supporting evidence for details (target environment of tunnel opening, selection of construction equipment for tunneling operation, estimation of dust/toxic gas emission and the necessary ventilation capacity, plan of ventilation system with flexible ducts and dust collector)

- Treatment at source of dust generation

- Measurement, evaluation, treatment and recording of dust concentration

- Maintenance of ventilation system

- Use of respiratory protective equipment

- Occupational health education

- Installation of facilities for rest

And shall comply with the requirements of these Specifications.

(b)	System Configuration

The ventilation system adopts a longitudinal-flow jet fan, for which ventilation equipment consists of the following equipment:

- Jet Fan Equipment

- Ventilation Control Equipment

- Measuring Equipment

(c)	Applicable Standards

The System shall comply with these Specifications, and laws, regulations, rules and specifications listed in the following table.

Applicable Standards

Technical Standards of Tunnel Ventilation. Japan Road Association 2008

Standard Design Specifications Vol. 7 Machinery, Book 2 Tunnel Ventilation Facilities. NEXCO RI 2015

Traffic Volume of Road. Japan Road Association 1984

Road Tunnel Emergency Facilities Installation, Standards and Remarks. Japan Road Association 2001

The system shall be manufactured, installed, tested and commissioned in accordance with ISO 9001 compliant quality assurance and quality control systems. Manufacturers must be organizations granted an ISO 9001 certificate by a public independent body.

(d)	Scope of Works for Ventilation System

Table 55-1 describes the scope of works that shall be performed for the establishment of the Ventilation System.

The Contractor shall also explain the system operation to the Facility Manager before completion, and this explanation of operation shall also be included in the construction scope of this project.

Table 55-1: Scope of Work for Ventilation System

| Equipment/Facility | Unit | Qty. | Construction Content |
| --- | --- | --- | --- |
| Jet fan. Model JFX-1250 | Units | 15 | Fabrication and installation |
| Soot visibility measuring equipment | Set | 2 | Fabrication and installation |
| Carbon monoxide measuring equipment | Units | 2 | Fabrication and installation |
| Air flow direction and velocity meter | Units | 2 | Fabrication and installation |
| Ventilation measurement control board | Panel | 1 | Fabrication and installation |
| Ventilation operation board | Panel | 1 | Fabrication and installation |
| Ventilation inverter control board | Panel | 4 | Fabrication and installation |
| Manual switchbox (for 2 units). Class 1 heat-resistant specifications | Panel | 4 | Fabrication and installation |
| Manual switchbox (for 2 units) | Panel | 3 | Fabrication and installation |
| Manual switchbox (for 1 unit) | Panel | 1 | Fabrication and installation |
| Power conduit between each equipment and board. Scope shall be based on drawings. | Set | 1 | Installation |
| Inspection | Set | 1 |  |
| Comprehensive commissioning adjustments | Set | 1 |  |

(e)	Design Criteria

The required structural and traffic conditions for the design of ventilation facilities are the following: (Refer to Table 55-2)

(i)	Traffic method:  Two-lanes, two-ways of traffic

(ii) 	Design speed:  60 km/h

(iii) 	Tunnel length and inclination

- Lr=2688m, +3.5%:2649m, -0.5%:39m

(iv) 	Tunnel cross sectional area:  Ar=71.6m2

(v)	Hydraulic diameter Dr

Hydraulic diameter can be calculated from the following equation

Dr=4*Ar/Sr *Sr : Cross section perimeter (Sr=32.9m)

Hydraulic diameter is as follows from the equation:  Dr=8.7 m

(vi) 	Lane width: 3.5 m

(vii) 	Shoulder width: 0.5 m

(viii)	Altitude: 1292–1385 m, avg. 1339 m

(2)	Basic Requirements

(a)	Basic Design

(i)	Ventilation system: Longitudinal-flow jet fan

(ii) 	Ventilation control method

Normal control: Feed-Back (FB) control, program control (as backup in case FB control fails)

Emergency control: fire connected control (low-speed ventilation control), fire manual control.

(iii)	Jet fan placement

Four jet fans are required to serve as evacuation support control (low-speed ventilation control) and firefighting support control (exhausting). For the low-speed ventilation control, if a jet fan runs within 500 m in front or behind the fire point, it will cause smoke to spread and hinder evacuation conditions. Thus, jet fans located within 500 m in front or behind a fire point must not run during a fire.

To ensure this, jet fans are positioned near the portals on each end to permit low-speed ventilation control regardless of the fire point position.

(iv)	Operation

During normal conditions, the ventilation measurement control board in the Eastern Power Room collects measured data from VI, CO, and AV meters, determines the proper ventilation volume and direction, and sends run/stop commands to the ventilation inverter control board as well as ventilation control center (a separate project).

During fire conditions, after the fire emergency signal is input, normal control is immediately suspended and the system switches to low-speed ventilation control to improve evacuation conditions. Once evacuation is complete, firefighting support is provided via fire manual control.

Table 55-2: Design Criteria

| Item | Description |
| --- | --- |
| Tunnel | 2688 m |
| Longitudinal Section |  |
| Cross Section |  |
| Cross Section Area | Ar = 71.6 m2 |
| Traffic Conditions | 2-lanes, 2-ways of traffic |
| Designed Speed | 60 km/h |

(b)	Durability

The system shall be operated 24 hours a day, 365 days a year, the hardware must be durable for continuous operation.

(c)	Facility Expandability

Ventilation equipment has been strengthened due to the world environmental considerations regarding to the global warming and the regulations global climate issues are strictly addressed to control and minimize the automobile’s gas emission.

To address future equipment changes or modifications, the system must be easily adaptable, and shall facilitate the installation of additional basic equipment, etc., in a relative ease way.

(d)	Supplied Power

Ventilation inverter control board:

- from the ventilation transformer board:  3-phase 3-wire 415V 50 Hz

- from the ventilation measurement control board:  single-phase 2-wire 105V 50 HZ

Tunnel measuring equipment:

- from on-site transformer board:  single-phase 2-wire 220V 50 HZ

Ventilation measurement control board, ventilation operation board:

- from the I/O board:  single-phase 2-wire 105V 50 HZ

(3)	Ventilation Control Equipment

(a)		System Overview

An outline of the system for facilities is described below:

(i)	Control under normal conditions

During normal conditions, the ventilation measurement control board in the Eastern Power Room collects measured data from VI, CO, and AV meters, determines the proper ventilation volume and direction, and sends run/stop commands to the ventilation inverter control board and ventilation control center (a separate project).

It must be possible to use program control or manual control modes as a backup if measurement control fails.

(ii)	Control under emergency conditions

Once a fire signal is input, normal control is immediately suspended and the system switches to fire connected control (low-speed ventilation control) to improve evacuation conditions. After evacuation is complete, firefighting support is provided via fire manual control.

Low-speed ventilation control, which is implemented to prevent the spread of smoke from the fire, shall be implemented as follows:

- Control starts within 30 seconds after a fire is detected.

- Wind speed is lowered to approximately ± 2 m/s below wind speed at the roadway within 90 seconds after fire detection.

- Wind speed is lowered to approximately ± 0.5 m/s below wind speed at the roadway within 210 seconds after fire detection.

- Wind speed shall remain at approximately ± 0.5 m/s below wind speed at the roadway until evacuation is complete.

- Measurement signal processing

Measured data shall be averaged by a measurement processing unit that is incorporated into the ventilation measurement control board installed in the Eastern Power Room.

(iv)	Control and monitoring of west jet fans

Control and monitoring of jet fans installed on the west side shall be performed by the ventilation operation board installed in the Western Power Room.

The ventilation interlock shall have protective function for times when jet fans are switched between forward and reverse as well as a fire manual control function.

(v)	Inverter control

The eight jet fans used for fire control shall employ inverter control (rotation speed control) in order to ensure the responsiveness of low-speed ventilation control and to provide energy savings for ventilation in regular operation, and the rest 7 jet fans shall employ unit number control

(vi)	Control and monitoring from a remote supervisory control facility (separate facility)

Switching of control modes, manual control, etc., and state monitoring from a remote supervisory control facility (separate facility) must be possible.

(b)	Location of Use

The location of use shall be indoors at the Eastern Power Room and West Power Room.

(c)	Ambient Conditions

Temperature:  Indoor 0°C to +40°C

Humidity: Indoor 10% to 85% RH

Note that there must be no condensation.

(d)	Structure

The structure of each unit shall be as described below:

Table 55-3: Configuration of Ventilation Control Facilities

| Item | Description | Standards | Unit | Qty. | Location |
| --- | --- | --- | --- | --- | --- |
| Ventilation measurement control board | Indoor freestanding enclosed control panel | JEM 1459 | Panel | 1 | Eastern Power Room |
| Ventilation operation board | Indoor freestanding enclosed control panel | JEM 1459 | Panel | 1 | Eastern Power Room |
| Ventilation inverter control board | Indoor freestanding enclosed type | JEM 1425 | Panel | 2 | Eastern Power Room |
|  |  |  | Panel | 2 | Western Power Room |

The enclosure shall be durable and highly resistant to rusting, and have performance equal to or better than steel plate (hot rolled steel sheet).

Installation of freestanding equipment shall include seismic countermeasures to prevent accidents such as horizontal shifting, overturning, falling, etc., in the event of an earthquake.

Temperature rises in the board's internal components and various parts shall meet compliance standards under the conditions listed above in Ambient Conditions, and remain within a temperature range not detrimental to any part.

(e)	Ventilation Measurement Control Board and Ventilation Operation Board Specifications

(i)	Major fittings

The major fittings of the ventilation measurement control board and ventilation operation board are as follows:

Table 55-4: Major Fittings of the Ventilation Measurement Control Board

| Item | Equipment | Ventilation measurement Control board | Ventilation operation board |
| --- | --- | --- | --- |
| Major board-mounted fittings | Indicator light array: Indication of operation and failure | ○ | ○ |
|  | Control mode switchover switch: Push button | ○ | ○ |
|  | Manual control switch | ○ | － |
|  | Fire manual control switch | ○ | ○ |
|  | Alarm, failure return, lamp test switch | ○ | ○ |
|  | Graphic panel (touch-panel type) Display operation and measured values Set airflow for each notch's jet fan Set control target values, control cycle, etc. Set protection timer Set program control Set date/time Failure history | ○ | － |
| Control unit |  | ○ | ○ |
| Measurement processing unit | VI processing Unit, CO processing unit, AV processing unit | ○ | － |
| Recording unit |  | ○ | － |
| Power supply |  | ○ | ○ |
| Interface | For measurement equipment | ○ | － |
|  | For ventilation inverter board | ○ | － |
|  | For ventilation control center | ○ | － |
|  | For ventilation operation board | ○ | － |
|  | For ventilation measurement control board | － | ○ |
|  | For power receiving and distribution facilities | ○ | － |
|  | For emergency equipment | ○ | － |
|  | For remote supervisory control facility | ○ | － |

(ii)	Control switchover

The ventilation control block is as shown in the drawings. The control switchover and operating locations shall be as described below.

Table 55-5: Control Switchover and Operating Locations

| Operation | Content | Operating location |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Ventilation measurement Control board | Ventilation Interlocking board | Remote monitoring Control unit (separate equipment) | Ventilation INV Board | Ventilation C/C Board (separate) |
| Running mode switchover | Independent–Interconnected | ○ | ○ | － | － | － |
| Operating location switchover | Remote–Direct | ○ | － | ○ | － | － |
| User-operation mode switchover | Auto–Manual | ○ | － | ○ | － | － |
| Control method switchover | Measurement–Program | ○ | － | ○ | － | － |
| Manual airflow-direction control | Forward–Reverse | ○ | － | ○ | － | － |
| Manual notch operation | Notches 0–8 | ○ | － | ○ | － | － |
| Fire control system mode switchover | Fire (connected)–Fire (manual) | ○ | ○ | ○ | － | － |
| Fire-mode manual notch operation | Forward, reverse, stop | ○ | ○ | ○ | － | － |
| Independent operation (independent control) | Operate–Stop | － | － | － | ○ | ○ |

(iii)	Control functions of the ventilation measurement control board and ventilation operation board shall be as described below:

Table 55-6: Control Switchover and Operating Location

| Function | Purpose | Ventilation measurement Control board | Ventilation Interlocking board |
| --- | --- | --- | --- |
| Connected control | Manual control, automatic control, fire manual control switch, fire connected control | ○ | － |
| Manual control | Notch control is initiated by an operating switch on the ventilation control board during inspections or when automatic measurement control has failed. There shall be roughly 0–8 air flow notches. | ○ | － |
| Automatic control | Perform measurement control or program control. | ○ | － |
| Measurement control (Notch configuration circuit) | Determine jet fan airflow volume and direction based on measurements from the VI, CO and AV meters in the tunnel. | ○ | － |
| Program control | Automatically perform a preset operating pattern as a backup when the automatic measurement control has failed. Air flow notches shall have a setting function with 4 patterns of 'Weekday, Holiday, Saturday, and Special Day', wherein 24 hours of setting is possible in 1 hour increments. It shall also be easy to set the number of units and airflow direction on-site. | ○ | － |
| Override control when concentrations worsen | During automatic control, override control of all ventilator fans is executed if VI or CO values deteriorate to abnormal levels. | ○ | － |
| Fire manual control | An operating switch drives fans in a normal or reverse direction to exhaust smoke in the event of a fire. | ○ | ○ |
| Fire connected control | Execute fire mode operation (low-speed ventilation control), which is automatically set when a fire hazard signal is input. | ○ | － |
| Exclusion of failed equipment/Compensation with operational equipment | Exclude jet fans that have failed and compensate with operational equipment. | ○ | － |
| Lead fan switching | Switch the leading fan in a nonstop rotational schedule ("rotary endless") to ensure that jet fan running times through the ventilation C/C board are spread equally among fans. | ○ | － |
| Sequential activation | Relating to jet fan control through ventilation C/C board, activate jet fans one at a time due to capacity of the power source. | ○ | － |
| Forward/reverse switching protection | Relating to jet fan control through ventilation C/C board, install a protective timer as sudden switching from forward to reverse puts excessive load on the motor. | ○ | ○ |
| Acceleration/deceleration time switching protection | Relating to jet fan control through the ventilation INV board, install a protective timer to protect the motor against sudden acceleration/deceleration of rotating speed. | ○ | ○ |
| Control during power failure | Switch to measurement control with four jet fans during a power failure due to limitations of in-house power generation. | ○ | － |
| Control during power recovery | In manual mode: Continue 0 notch In automatic mode: Use measurement control with measured values at time of power recovery | ○ | － |
| Operating switch | Switching between modes, operating air volume, etc., shall be performed by a push button switch. | ○ | ○ |
| Touch panel | Display of jet fan operation and measured values Set/change the number of operating fans, target concentration, program, date and time, etc., by notch. View failure history | ○ | － |
| Array and status display unit | Fault indicator lamp lights to indicate a failed device. Status indicator lamp lights to indicate control and operating status of jet fans. | ○ | － |
| Measurement processing | Data required for ventilation control is processed upon receiving a measurement signal from monitoring equipment in the tunnel. | ○ | － |
| Recording unit | At least six months of data is recorded for number of jet fan notches and VI/CO/AV values. | ○ | － |
| Alarm processing | A warning buzzer sounds when equipment has failed. | ○ | ○ |

(iv)	Signal connection between ventilation measurement control board and other boards

The number of signal connections between the ventilation measurement control board and other boards is as below.

Table 55-7: Number of Signal Connections on Ventilation Measurement Control Board

| Equipment | Type | Number of points (Max. number) | Interface |
| --- | --- | --- | --- |
| Measuring equipment | Monitoring | 38 | Contact: DC 24V 50mA or more |
|  | Measurement | 6 | DC 4–20mA |
| Ventilation operation board | Control | 9 | Contact: DC 24V 50mA or more |
|  | Control (INV airflow) | 1 | Analog: DC 4–20mA |
|  | Monitoring | 21 | Contact: DC 24V 50mA or more |
| Ventilation inverter board (1) Eastern Power Room | Control | 4 | Contact: DC 24V 50mA or more |
|  | Control (INV airflow) | 1 | Analog: DC 4–20mA |
|  | Monitoring | 8 | Contact: DC 24V 50mA or more |
| Ventilation control Center (1) (2) Eastern Power Room | Control | 7 | Contact: DC 110V 50mA or more |
|  | Monitoring | 8 | Contact: DC 24V 50mA or more |
| Relay terminal board (distributors) | Monitoring | 2 | Contact: DC 24V 50mA or more |
| Relay terminal board (for emergency use) | Monitoring | 2 | Contact: DC 24V 50mA or more |
| Relay terminal board (remote supervisory control facility) | Control | 19 | Contact: DC 24V 50mA or more |
|  | Monitoring | 72 | Contact: DC 24V 50mA or more |
|  | Measurement | 6 | Analog: DC 4–20mA |

Table 55-8: Number of Signal Connections on Ventilation Operation Board

| Equipment | Type | Number of points (Max. number) | Interface |
| --- | --- | --- | --- |
| Ventilation inverter board (1) Western Power Room | Control | 4 | Contact: DC 24V 50mA or more |
|  | Control (INV airflow) | 1 | Analog: DC 4–20mA |
|  | Monitoring | 8 | Contact: DC 24V 50mA or more |
| Ventilation control center (1) Western Power Room | Control | 7 | Contact: DC 110V 50mA or more |
|  | Monitoring | 8 | Contact: DC 24V 50mA or more |
| Ventilation control Center (2) Eastern Electric Room | Control | 4 | Contact: DC 110V 50mA or more |
|  | Monitoring | 4 | Contact: DC 24V 50mA or more |

(f)	Ventilation Inverter Control Board Specifications

(i)	Major fittings

The ventilation inverter control board consists of a main board and sub board with 2 panels/4 jet fans. Major fittings on both panels shall be as follows.

Table 55-9: Major Fittings on the Ventilation Inverter Board

| Item | Equipment | Ventilation inverter board (1) (main board) | Ventilation inverter board (2) (sub board) |
| --- | --- | --- | --- |
| Major fittings | Controller | ○ | － |
|  | Programmable display (display of jet fan and inverter operating status as well as independent control of jet fans) | ○ | － |
|  | Inverter section - Circuit breaker - 12-phase rectifier transformer - AC reactor - Input noise filter - AC drive - Feedback type sine wave filter - Zero-phase AC unit - Earth-fault overcurrent relay | ○ | ○ |
| Interface | Ventilation measurement control board or ventilation operation board | ○ | － |

(ii)	Specifications

Measures to control high harmonics

The harmonic control method shall be a feedback type sinusoidal filter.

Harmonic current shall be under the maximum values listed in the table below:

Table 55-10: Maximum Harmonic Current per 1 kW Contract Command

(Units: mA/kW)

| Receiving-side voltage | 5th order | 7th order | 11th order | 13th order | 17th order | 19th order | 23rd order | Over 23rd order |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 22 kV | 1.8 | 1.3 | 0.82 | 0.69 | 0.53 | 0.47 | 0.39 | 0.36 |

Measures to control surge voltage:  Output voltage amplitude shall no more than 700V to inhibit surge voltage generated by jet fan motors.

Measures to control noise:  Leakage current shall be no more than 300mA to inhibit noise to AM radio broadcast waves and metal circuits from electromagnetic noise.

(4)	Jet Fan Equipment

(a)	Application

This section applies to jet fans and other equipment (collectively referred to as “equipment”).

(b)	Equipment Overview

(i)	Location of Use

Location of use shall be inside the tunnel.

(ii)	Ambient Conditions

Temperatures:  Outdoor  - 10°C to + 40°C

Humidity:  Outdoor	85% RH maximum

(c)	Structure

(i)	Equipment configuration

Table 55-11: Jet Fan Equipment Configuration

| Equipment | Type | Specifications | Unit | Qty. |
| --- | --- | --- | --- | --- |
| Jet fan | Motor Driven In-Tunnel Axial Flow Type. High Velocity Type | JFX-1250 | Units | 15 |
| Hanging fittings |  |  | Set | 15 |
| Manual switchbox | Outdoor wall-mounted enclosed type | Class 1 heat resistance | Panel | 4 for 2 units |
|  |  |  | Panel | 3 for 2 units |
|  |  |  | Panel | 1 for one unit |

(ii)	Materials to be used

The following material, or alternatively material with equivalent or higher specifications shall be used.

Table 55-12: Material to be used for Jet Fan Equipment

| Category | Usage | Material/Standard | Standard |
| --- | --- | --- | --- |
| Jet fan | Casing | Stainless Steel Plate (SUS304) | JIS G 4303 |
|  | Perforated sheet metal | Stainless Steel Plate (SUS304) | JIS G 4303 |
|  | Exterior plate | Stainless Steel Plate (SUS304) | JIS G 4303 |
|  | Impeller | Aluminum alloy casting |  |
|  | Silencer | Glass wool |  |
| Hanging fittings | Hanging fittings | Rolled Steels for General Structure (SS400) | JIS G 3101 |
|  | Mechanical anchor bolts | Stainless Steel Plate (SUS304) | JIS G 4303 |
| Manual switchbox | Enclosure | Stainless Steel Plate (SUS304) | JIS G 4304 or JIS G 4305 |

(iii)	Coating: Coating and paint specifications for the jet fan shall be as shown below. Color of the top coat shall comply with instructions from supervision staff.

Table 55-13: Jet Fan Paint Specifications

| Painted parts | Surface treatment | Construction location | Process | Paint type | Standard thickness (μm) |
| --- | --- | --- | --- | --- | --- |
| Exterior and ventilation panel | Surface preparation by blasting, degreasing (wiping with solvent) | Factory | Primary primer | Epoxy primer | Total, min. 40 μm |
|  |  |  | Top coat | Epoxy resin paint |  |
| Impeller | Surface preparation by blasting Degreasing (wiping with solvent) | Factory | Undercoat | Epoxy resin paint | Total, min. 120 μm |
|  |  |  | Middle coat | Epoxy resin paint |  |
|  |  |  | Top coat | Epoxy resin paint |  |

Note 1:	In principle, factory painting shall be airless spray painted.

Note 2:	In principle, touch-up painting shall be brush painted.

Note 3:	Jet fan hanging fittings shall be zinc hot-dip galvanizing HDZ55 (JIS H8641).

However, threaded sections shall be HDZ35 galvanized.

(iv) 	Structure

Casing

- Casing shall be structured with appropriate detachable sections to make inspection and maintenance convenient.

- Casing shall comprise grade SUS304 austenite type stainless steel of JIS G 4304 (Hot-rolled Stainless Steel Plate, Sheet and Strip) or JIS G 4305 (Cold-rolled Stainless Steel Plate, Sheet and Strip) standards, with a steel plate welded structure frame and stainless-steel exterior plate of thickness at least 1.5 mm.

- Casing shall be structured to adequately attenuate noise by packing the casing's inner and outer cylinder wall with sound absorbing material, and protecting with a perforated stainless steel plate (SUS304, t=min. 1.5 mm) to prevent the sound absorbing material from dispersing during operation.

- Air inlet and discharge ports shall be of satisfactory shapes that minimize air flow separation, vortex formation, etc.

Electric motor

- The motor shall be a fully closed type with Class F insulation or better, and shall have sufficient dielectric strength and sealing performance to withstand the environments and air currents it will be subjected to in the tunnel.

- Between the motor and the casing, lead wires must not be directly exposed to airflow.

- In principle, bearings shall be rolling bearings, have ample ability to withstand long-term continuous operation, and have excellent sealing performance.

- The motor shall have ample ability to withstand the complicated start/stop etc. operation it will be subjected to in performing tunnel ventilation.

Impeller

- The impeller shall have corrosion resistance properties conforming to JIS H5202 (Aluminium Alloy Castings), JIS H4140 (Aluminium and Aluminium Alloy Forgings), or to equivalent or higher corrosion resistance. It shall also have excellent balance between operation and quietness, etc., and be sufficiently strong to withstand high-speed revolution.

- Impeller balance shall meet or exceed G6.3 of JIS B 0905 (Rotating Machines−Balance Quality Requirements of Rigid Rotors).

- Impeller mounting on the motor shaft shall be secure, stable, and have sufficient strength to withstand fatigue.

- Wing surfaces of the blades shall have a smooth and precise airfoil shape, and be of equal performance properties.

Hanging fittings

- Hanging fittings shall consist of metal hanging fittings and turnbuckles. The hanging fittings shall be attached to the tunnel ceiling with stainless steel anchor bolts and the jet fan shall be hung with turnbuckles.

- Hanging fittings shall have sufficient strength and durability with finished surfaces that conform to (HDZ55) (JIS H8641) Zinc Hot Dip Galvanizing.

Manual switchbox:  Switch box shall have an opening door in front and be secured in the back with stainless anchor bolts.

(d)	Jet Fan Specifications

The jet fan shall be composed of a casing, an impeller and an electric motor, etc. It shall have ample ability to withstand the water, smoke, dust, vehicle exhaust gas, etc., that it will be subjected to in the tunnel, and shall be structured in a manner that provides reasonably quiet operation. The jet fan shall be structured in a manner that conveniently facilitates tasks such as transporting, installation, disassembly, assembly, and cleaning, and its parts and assemblies shall have excellent compatibility.

Jet specifications shall be as follows:

Table 55-14: Jet Fan Specifications

| Painted parts | Surface treatment | Construction location | Process | Paint Type | Standard thickness (μm) |
| --- | --- | --- | --- | --- | --- |
| Exterior and ventilation panel | Surface preparation by blasting, degreasing (wiping with solvent) | Factory | Primary primer | Epoxy primer | Total, min. 40 μm |
|  |  |  | Top coat | Epoxy resin paint |  |
| Impeller | Surface preparation by blasting Degreasing (wiping with solvent) | Factory | Undercoat | Epoxy resin paint | Total, min. 120 μm |
|  |  |  | Middle coat | Epoxy resin paint |  |
|  |  |  | Top coat | Epoxy resin paint |  |

Note 1: 	Noise is the average value of two points, the inlet side and casing side

Note 2: 	The motor shall conform to JIS C 4213 “Low-voltage: Three-phase Squirrel-cage Induction Motors (Low-voltage Top Runner Motor)”

(5)	Measuring Equipment

(a)	Equipment Overview

(i)	Location of Use: Location of use shall be inside the tunnel.

(ii)	Ambient Conditions

Temperature:   Outdoor  - 10°C to + 40°C

Humidity:   Outdoor  85% RH maximum

(iii)	Equipment configuration

Table 55-15: Measuring Equipment Configuration

| Equipment | Specifications | Unit | Qty. |
| --- | --- | --- | --- |
| Soot Visibility Measuring Equipment (VI Meter) | Optical fiber calibration | Set | 2 |
| Carbon Monoxide Measuring Equipment (CO Meter) | Controlled potential electrolysis | Units | 2 |
| Air Flow Direction and Velocity Meter (AV Meter) | Ultrasonic | Units | 2 |

(c)	Soot Visibility Measuring Equipment (VI Meter)

(i)	Equipment configuration

Equipment configuration per set shall be as follows

Light emitter (with power supply and control cable)

Light receiver (with power supply, control cable, and fiber optic cable)

Light emitter power supply box

Light receiver power supply box

(ii)	Equipment specifications

Measurement method:	Continuous optical modulation method or equivalent

Measurement target:

- Luminous visibility in the tunnel's atmosphere

- The overall spectral reflectance of the measurement is based on luminous sensitivity under tunnel lighting.

Measurement distance: 100 m (In case of 90 m, convert to a 100 m scale visibility)

Measurement range: Visibility 0–100%

Measurement accuracy:  Within ± 2% of the maximum scale value

Response time:  Within 10 seconds for 90% all graduations

Measurement output:  An electric signal corresponding to strength or weakness of intermittent light.

Measurement input:  Light emitter, max. 13VA; light receiver, max. 37VA

Contact output:  Power off of emitter/receiver sent to control unit

Contact input:  Calibration command from control unit

Calibration:  Automatic calibration method using optical fiber

Light source:  LED

Light receiving element:  Silicon photodiode

(iii) 	Structure

Light receiver

- Type: Outdoor wall-mounted type

- Material: Stainless steel plate SUS 304 (JIS G 4305)

- Light emitting/receiving components in particular shall be resistant to dust, splashing/dripping water, and humidity. The front lens must not cloud even when exposed to high outdoor humidity.

- Light emitting/receiving components shall have an inner cylinder that can be pulled out to facilitate easy cleaning of dust or other particulate matter inside the hood.

Power supply box

- Type: Outdoor wall-mounted type

- Material: Stainless steel plate SUS304 (JIS G 4304 or JIS G4305)

(d)	Carbon Monoxide Measuring Equipment (CO Meter)

(i) 	Equipment specifications

Equipment shall have the following specifications.

Measurement method: Continuous measurement with controlled potential electrolysis and a calibrating function.

Measurement target: Carbon monoxide in the air

Measurement range: 0-300 ppm as standard.

Calibration method: One manual calibration every six months using calibration gas

Repeatability:

- Within ±3 ppm at 0–150 ppm

- Within ±10 ppm at 151–300 ppm

Measurement accuracy:

- Within ±6 ppm at 0–150 ppm

- Within ±15 ppm at 151–300 ppm

(Under once-per-month calibration conditions)

Response time: 90% of responses within 2 min 30 sec or less (conduit length not included)

Measurement output: C 4–20mA

Contact output: Contact output to the control unit is as follows:

- Flow rate decrease

- Power off

- Checking

Sampling point filter:  Built-in type

(ii) 	Structure

The structure shall comprise steel plated outer covering, have excellent electrical properties, mechanical durability, and anticorrosive properties, and shall also be easy to perform inspection and maintenance on. In terms of design, it must be fabricated in a manner that includes resistance to vehicle emissions, splashing/dripping water, humidity and other concerns.

Type and material:

- Type: Outdoor wall-mounted enclosed type or outdoor freestanding enclosed type (JEM 1459)

- Material: Stainless steel plate SUS 304 (JIS G 4305)

(f)	Air Flow Direction and Velocity Meter (AV Meter)

(i)	Equipment configuration

The wind direction wind speed measurement device in the tunnel shall consist of a measurement unit and control unit. Configuration per set of air flow direction and velocity meter (AV meter) shall be as below.

Ultrasonic probe (detector) : 1 unit

Converter box (holds the converter): 1 unit

Probe converter cable (accessory) : 1 pair

(ii) 	Equipment specifications

Measurement method:  Coordinate conversion of two component wind speeds by time division duplexer type ultrasonic pulse propagation

Measurement direction:  In a horizontal direction parallel to the tunnel wall

Measurement range:  0 to ± 15m/s

Measurement accuracy:  Within ± 4% of the maximum scale value (within ± 0.3 m/s if wind speed is 5.0 m/s or less)

Responsivity:  Average travel time, 10 sec (sampling time: 0.05 seconds)

Contact output:

Items output to the control unit are as follows:

- Failure

- Checking

Calibration:  Zero and full-scale power calibration by manual switch

(iii)	Structure

Type and material (converter)

- Type: Outdoor wall-mounted enclosed type

- Material: Stainless steel plate SUS304 (JIS G 4304 or JIS G4305)

(6)	Spare Parts

(a)	Ventilation Control Equipment

Table 55-16: Spare Parts for the Ventilation Measurement Control Board and Ventilation Operation Board

| Part | Specifications | Qty. |
| --- | --- | --- |
| Various fuses | － | 100% |
| Relay | Excluding printed board mounting hardware | 1 of each type |

While manufacturer's standards must be followed regarding spare parts for the ventilation inverter control board, the following parts, which are expected to need replacing within 10 years of service, must also be prepared as spare parts.

Table 55-17: Spare Parts for Ventilation Inverter Control Board

| Equipment Category | Product | Qty. |
| --- | --- | --- |
| AC drive | Inverter unit | 2 pc. One in each power room |
| Sequencer etc. | Internal battery | 2 pc. |
|  | CPU unit | 2 set |
|  | Touch panel | 2 set |
|  | Other units | 2 set |
| Other | Board cooling fan | 4 pc. Number for all boards |
|  | DFSA condenser | 8 pc. Amount for jet fans |

(b)	Measuring Equipment

Table 55-18: Spare Parts for Soot Visibility Measuring Equipment (VI Meter)

| Part | Specifications | Qty. |
| --- | --- | --- |
| Fuse | － | 100% |
| VI meter light source lamp | LED | 100% |

Table 55-19: Spare Parts for Carbon Monoxide Measuring Equipment (CO Meter)

| Part | Qty. |
| --- | --- |
| Fuse | 100% |
| Filter element | 100% |
| Relay | 1 of each type |
| NOx absorbent | 1 set / 500g |
| Span gas cylinder | 1 pcs. |
| Pressure reducing valve | 1 pc. |
| Connection tube | 1 set 1 m (including accessories) |

Table 55-20: Spare Parts for Air Flow Direction and Velocity Meter (AV Meter)

| Part | Specifications | Qty. |
| --- | --- | --- |
| Fuse | － | 100% |

(7)	INSPECTION AND TESTING ADJUSTMENTS

(a)	Inspection (including checks) On-Site Verification by Supervision Staff

This project's stage-reviews shall be as follows. Note that the review method and schedule must be decided in consultation with supervisory staff.

Materials verification (jet fan, measuring, and ventilation control equipment)

Dimensions verification (jet fan, measuring, and ventilation control equipment)

Functions verification (jet fan, measuring, and ventilation control equipment)

Performance check (jet fan, measuring, and ventilation control equipment)

Paint/coatings verification (jet fan, measuring, and ventilation control equipment)

On-site commissioning adjustments (equipment overall)

The above verifications and checks shall be carried out in accordance with the following schedule:

Table 55-21: Items for Inspection and On-Site Verification

| Sub-item | Implementation period |
| --- | --- |
| - Materials verification | (Factory) After delivery, before production begins (Site) After delivery, before installation begins |
| - Dimensions verification | (Factory) During trial shop assembly (Site) When installation completes |
| - Functions verification | (Factory) When trial shop assembly completes (Site) When installation completes |
| - Dimensions verification | (Factory) When production completes (Site) When installation completes |
| - Paint/coatings verification | (Factory) When production completes (Site) When installation completes |
| - On-site commissioning adjustments | (Site) When installation completes |

(b)	Inspection and Testing Adjustments

(i) 	Materials verification

During factory production:  In managing materials, the materials shall be verified based on the materials and other items listed in this Specifications document and Approved Drawings.

- Jet fan equipment shall also undergo non-destructive testing.

| Item to be Verified |  | Remarks |
| --- | --- | --- |
| Impeller | Blades | Radiographic flaw detection (all items) |
|  |  | Penetrant inspection (all items) +Radiographic flaw detection (10% of items) |
|  | Hub | X-ray flaw detection |
| Hanging fittings |  | Penetrant inspection (all items) |

When installed at site:  Electrical materials to be used during site installation shall be inspected when delivered to the site.

(ii)	Dimensions verification

During factory production

| Item to be Verified |  |  |  |
| --- | --- | --- | --- |
| Jet fan equipment | External dimensions |  | Diameter |
|  |  |  | Length (in axial direction) |
|  | Hanging fitting dimensions |  |  |
|  | Gaps between impeller tip and casing |  |  |
| Measuring and ventilation control equipment | External dimensions | Assembled state |  |
|  | External appearance | Placement of board mounted fixtures |  |

When installed at site

| Item to be Verified |  |  | Remarks |
| --- | --- | --- | --- |
| Jet fan equipment | Anchor bolt static load test |  | 29.5 KN (over 15 times actual load) |
|  | Distance between casing and road surface |  | Past clearance |
|  | Installation spacing | Portal distance |  |
|  |  | Distance between jet fans |  |
| Measuring and ventilation control equipment | Installation lcation | Placement distance |  |
|  |  | Installation height |  |

(iii)	Functions verification

During factory production

| Item to be Verified |  |  | Remarks |
| --- | --- | --- | --- |
| Jet fan equipment | Anchor bolt static load test |  | 29.5 KN (over 15 times actual load) |
|  | Distance between casing and road surface |  | Past clearance |
|  | Installation spacing | Portal distance |  |
|  |  | Distance between jet fans |  |
| Measuring and ventilation control equipment | Installation location | Placement distance |  |
|  |  | Installation height |  |

When installed at site

| Item to be Verified |  | Reference standard | Remarks |
| --- | --- | --- | --- |
| Jet fan equipment | Voltage | Internal standards | Verify values |
|  | Current |  |  |
|  | Power |  |  |
|  | Vibration | JIS B 8364 | Shall be according to Approved Drawings |
| VI meter | Light emitter/receiver reference voltage |  | Shall be according to Approved Drawings |
|  | Contact signal input/output |  |  |
|  | Communication function, fault signal |  |  |
|  | Precision of operation, responsivity |  |  |
| CO meter | Operating test |  | Shall be according to Approved Drawings |
|  | Reproducibility |  |  |
|  | Alarm output |  |  |
| AV meter | Output |  | Shall be according to Approved Drawings |
|  | Operating conditions |  |  |
| Ventilation Control Equipment | Lamp test |  | All lamps must illuminate |
|  | Insulation resistance |  | Shall meet or exceed specified value |
|  | Ground resistance |  | Shall meet or exceed specified value |
| Verifying measures to control high harmonics | High harmonic current |  | Shall not exceed the values listed in this Detailed Technical Specification |
|  | Output voltage amplitude at the manual switchbox terminal block |  |  |
|  | Leakage current |  |  |

(iii)	Performance test

During factory production

| Item to be Verified |  | Reference standard | Remarks |
| --- | --- | --- | --- |
| Jet fan | Rotational speed | JIS B 8330 | Verify rotational speed and direction |
|  | Air flow (volume) |  | Shall meet or exceed specified value |
|  | Wind pressure |  |  |
|  | Voltage |  | Verify values |
|  | Current |  |  |
|  | Power |  |  |
|  | Shaft power |  | Shall not exceed electric motor output |
|  | Bearing vibration |  | Vibration tolerance shall conform to JIS B 8330 Measurement points shall be according to Approved Drawings |
|  | Noise | JIS B 8346 | Shall be according to Approved Drawings |
|  | Starting time and starting current until reaching rated rotation |  | Verify values |
|  | Moving parts inside the casing |  | Visual confirmation (after Performance Check test run) |
| Motor | Insulation resistance test | JIS C 4213 JEC 2713 JIS 4034-1 | Shall be according to Approved Drawings |
|  | Withstand voltage test |  | Shall withstand the test voltage |
|  | Temperature test |  | Shall be according to Approved Drawings |
|  | Characteristics test |  |  |
| VI meter | Accuracy automated test |  | Shall be according to Approved Drawings |
|  | Response speed |  |  |
|  | Insulation resistance test |  |  |
|  | Dielectric strength test |  |  |
|  | Power consumption |  |  |
| CO meter | Reproducibility |  | Shall be according to Approved Drawings |
|  | Response speed |  |  |
|  | Check fluctuation of power supply voltage |  |  |
| AV meter | Output |  | Shall be according to Approved Drawings |
|  | Operating conditions |  |  |
|  | Voltage |  |  |
| Ventilation Control Equipment | Insulation resistance test |  | Shall be according to Approved Drawings |
|  | Grounding resistance test |  |  |
| Measures to control high harmonics | High harmonic current measurement |  | Verify values |
|  | Measure output voltage amplitude at the manual switchbox terminal block |  |  |
|  | Measure leakage current |  |  |

When installed at site

- Verify that site results match the performance check at the time of factory production.

(iv)	Paint/coatings verification

For paint/coating verification, conduct visual inspection of base material, coating thickness, and coating appearance during factory production.

When installed at site, perform visual inspection of paint/coating.

(v)	On-site commissioning adjustments

| Item to be Verified |  | Remarks |
| --- | --- | --- |
| Comprehensive commissioning | Vibration | There must be no abnormal vibration |
|  | Noise | There must be no abnormal noise |
| Mechanism operation test |  | Check the operation of the instrument panel commands, illumination of indicator lights, and operation of various switches. |
| Sequence test | Interlock | Verify that each control mode works properly Verify the operation of alarms, etc., during failure |
|  | Protective circuit formation | Verify the time from protection circuit formation to stop (warning) |
| Ventilation air velocity test |  | Measure air velocity and natural wind speed in the tunnel at each equipment and notch |
| Comprehensive interoperability test | Verify interoperability of the remote supervisory control facility | Each monitoring and control item must operate properly |
|  | Interoperability test with emergency equipment and firefighting equipment | Fire signal and fire point must be properly input |
|  | Interoperability test with power receiving and distribution equipment | Power failure and recovery control modes must operate properly |

5600.	TUNNEL FIRE FIGHTING SYSTEM

(1)		Fire Hydrants

(a)	Overview and Configuration

Fire hydrants are installed on the inner wall of the tunnel. By operating the handle provided on the front of the ‘fore tilting door’ containing a nozzle, hydrant opening lever, etc., it will tilt forward to provide the tools necessary to extinguish fires. The equipment configuration shall be as follows:

| Item | Quantity |  |
| --- | --- | --- |
|  | Type A Hydrant | Type B Hydrant |
| Cabinet box | 1 set | 1 set |
| Shelf | 1 set | 1 set |
| Nozzle | 1 set | 1 set |
| Hose | 1 pc. | 1 pc. |
| Hose guide | 1 set | 1 set |
| Red signal light | 1 pc. | 1 pc. |
| Fire hydrant valve | 1 pc. | 1 pc. |
| Automatic pressure regulating valve | 1 pc. | 1 pc. |
| Combined automatic drainage and air release valve | 1 pc. | 1 pc. |
| Pump activation switch | 1 pc. | 1 pc. |
| Pump activation interlock switch | 1 pc. | 1 pc. |
| Push button alarm | 1 pc. | 1 pc. |
| Telephone jack | 1 pc. | 1 pc. |
| Circuit terminal | 1 set | 1 set |
| Equipment name plate | 1 set | 1 set |
| Water supply outlet | － | 1 pc. |
| Fire extinguisher | 2 pc. | 2 pc. |
| Maintenance valve | 1 pc. | 1 pc. |
| Other accessories | 1 set | 1 set |

(b)	Specifications

(i)	Type: Fore tilting door with internal hose-attached fire hydrant

(ii)	Operating pressure range: 0.47–1.77 MPa (5–18 kgf/cm2)

(iii)	Cabinet box

- The cabinet box shall have a structure divided into front cabinet A and rear cabinet B which are assembled with stainless steel bolts (SUS304). The cabinet box shall also have a plate attached that lists the name, type, manufacture date, manufacture number, and manufacturer name. The fire hydrant's fore tilting door shall be equipped with a handle, grip, equipment nameplate and instruction plate.

Material

- Cabinet box: SUS304

- Handle: SCS13

Coating:  After applying heat-cured epoxy powder coating, the front surface and visible frame surface shall be finished with a urethane resin coating.

(iv)	Shelf

Material: SUS304 shaped steel

Surface treatment: Unpainted

(v)	Nozzle

The nozzle shall be able to change the shape of discharged water stream between a straight stream pattern and wide spray pattern.

Type:  Grip head switchable variable spray nozzle

Discharge water pressure and flow rate:

- Straight stream pattern 	0.29 MPa (3.0 kgf/cm2) 130L/min (-0% to +10%)

- Wide spray pattern 	0.29 MPa (3.0gf/cm2) 130L/min (-0% to +10%)

Effective range:  min. 20 m (when using straight stream)

Maximum spray expansion angle:  100°

Nominal diameter: 	 40A

Material:  AC7A

(vi)	Hose

The hose shall be shape-retaining and stored in its wrapped form inside the box.

Type:  shape-retaining gummed cloth hose

Stored length:  30 m

Nominal diameter:  32A

Material:  Main material, polyester

(vii)	Hose guide

The fore tilting door shall have a hose guide attached to ensure the hose can be pulled out smoothly.

Material:  SUS304

(viii)	Fire hydrant valve

The fire hydrant valve shall be equipped with a cam which causes an interlock switch to activate when the ball valve, which is opened/closed via a connected wire, is operated by lever on the fore tilting door.

Type:  Ball valve

Nominal diameter:  32A

Material

- Body:  CAC406

- Wire:  SUS304

(ix)	Automatic pressure regulating valve

An automatic pressure regulating valve shall be provided to adjust the discharge pressure of the nozzle, keeping it constant regardless of fluctuation in the hydrant's primary pressure. Its specifications shall be as follows.

Type: Bellofram type automatic pressure regulating valve

Nominal diameter: 32A

Material: CAC406

(x)	Combined automatic drainage and air release valve

There shall be valve that combines the functions of draining residual water that has collected in the fire hydrant valve's secondary side, and aspirate the air required to drain water that remains in the hose after being used to discharge water.

Type: Flat seated automatic drain valve/air release valve

Nominal diameter:  15A

Material:  CAC406

(xi)	Red signal light

Type:  Jetproof structure

Lamp:  LED lamp

Cover globe:  Red methacrylic resin

Rating:  AC 100V ± 10% 10mA

(xii)	Pump activation switch

Type:  Jetproof structure with non-locking push button switch

Contact rating:  AC 110V/DC 110V 5A/2.2A

Contact configuration:  1a

(xiii)	Pump activation interlock switch

Type:  Jetproof structure, limit switch

Contact rating:  AC 125V/DC 125V 10A/0.4A

Contact configuration:  1a

(xiv)	Push button alarm

The push button notification system shall conform to the standards set by the Ministry of Home Affairs for P-type Grade 1 Transmitting Devices, and shall be constructed with a jetproof push button switch.

Transmitter body

- Material

        - Body:  SUS304

        - Resin glass:  Methacrylic resin

- Coating:	Uncoated

Push button switch

- Type:  Non-locking push button switch

- Contact rating:  AC 110V/DC 110V 5A/2.2A

- Contact configuration:   1a, 1b

(xv) 	Telephone jack

Type: 	 Plug-in telephone jack

Standard:  Japan Fire Alarms Manufacturer's Association, Unified Standard

(xvi)	Circuit terminal

A terminal block shall be set inside a sealed cabinet box with a jetproof structure that includes cable connectors at the cable feed-in/draw-out location.

Cabinet box

- Material

        - Body:  ABS resin

        - Lid:  Polycarbonate resin

Terminal block

- Synthetic resin

(xvii)	Water supply outlet (Type B fire hydrant only)

The hydrants, which supply water to firefighting vehicles, etc., shall have the following specifications.

Format:  65A×90° fire department dedicated outlet tap

Nominal diameter:  65A

Hose connection method:  Plug-in type

Material:  CAC406

(xviii)	Fire extinguisher

Type:  ABC powder type fire extinguisher, 6.0 kg

Extinguishable fire types:  A-5, B-12, C-1

Skirt:  Corrosion resistant coating

(xix)	Maintenance valve

A maintenance valve shall be provided to temporarily interrupt water supply to the hose to allow maintenance and inspection to be conducted. Its specifications shall be as follows.

Type:  Spring-type flow switching valve

Nominal diameter:  32A

Material:  CAC406

(2)	Exterior Water Supply Outlet

(a)	Overview

An exterior water supply outlet shall be installed near the tunnel entrance for firefighting as well as to provide water to fire engines and for tunnel cleaning, etc.

A water supply outlet shall also be installed near the tunnel entrance to enable fire engines, etc. to supply water to the distribution main.

(b)	Specifications

(i)	Water supply outlet

Type:  Wall embedded dual outlet water supply outlet

Discharge port:  65 mm×2 outlets

Hose connection port:  Plug-in type

Material

- Body:  FCD450

- Main section:  CAC406

Maximum working pressure

- East portal:  1.37 MPa (14 kgf/cm2)

- West portal:  1.77 MPa (18 kgf/cm2)

Connection flange

- East portal:  JIS10K FF 100A

- West portal:  JIS16K FF 100A

(ii)	Water outlet

Type:  Wall embedded dual outlet

Discharge port:  65 mm×2 outlets

Hose connection port:  Plug-in type

Material

- Body:  FCD450

- Main section:  CAC406

Maximum working pressure

- East portal:  1.37 MPa (14 kgf/cm2)

- West portal:  1.77 MPa (18 kgf/cm2)

Connection flange

- East portal:  JIS10K FF 100A

- West portal:  JIS16K FF 100A

(iii)	Coating

Inside:  Two coats of primer

Outside:  Two coats of a nickel primer under a silver painted finish.

- Parts, white bronze plating

(3)	Fire Pump

(a)	Overview and Specifications

Firefighting pumps are used to supply the water required by fire hydrants, water supply outlets and the like. They shall comply with the requirements of “Standard Specifications for Public Buildings Construction - Machine and Equipment Construction” (Volume 3, Chapter 1, para. 12, sect. 1.12.1) [published by “Japanese Public Buildings Association”, 2016 for the Ministry of Land, Infrastructure, Transport and Tourism of Japan] with the specifications listed below:

| Item |  | Specification |
| --- | --- | --- |
| Pump | Model | Multistage centrifugal pump |
|  | Discharge rate | 1190 l/min |
|  | Total pumping head | 59 m |
|  | Diameter | 125A×125A |
| Electric motor | Format | Fully enclosed splash-proof three-phase induction motor |
|  | Rating | Continuous |
|  | Output | 22 kW |
|  | Rated voltage | 400V |
|  | Rotational speed | 1500 rpm |
|  | Frequency | 50 Hz |
|  | Insulation type | Min. Class E |
|  | Activation method | Star-delta starting |
| Accessories |  | Compound pressure gauge Pressure gauge Drain cock Joint cover Phase flange Foundation bolt Nameplate Space heater Other necessary accessories |

(4)	Automatic Water Supply System

(a)	Overview and Specifications

The automatic water supply system consists of a pump and pressure tank. A drop in pressure in the pressure tank will activate the pump to supply of water to replenish water in the tunnel's water distribution main, compensate for water leaks, etc. They shall comply with “Standard Specifications for Public Buildings Construction - Machine and Equipment Construction” (Volume 5, Chapter 1, para. 2, sect. 1.2.3) [published by “Japanese Public Buildings Association”, 2016], with the specifications listed below:

| Item |  | Specification |
| --- | --- | --- |
| Pump | Model | Multistage centrifugal pump |
|  | Discharge rate | 60 l/min |
|  | Total pumping head | 11 m |
| Electric motor | Format | Fully enclosed splash-proof three-phase induction motor |
|  | Rating | Continuous |
|  | Output | 0.4 kW |
|  | Rated voltage | 3φ 3W 200V |
|  | Rotational speed | 3000 rpm |
|  | Frequency | 50 Hz |
|  | Insulation type | Min. Class E |
|  | Activation method | Direct activation |
| Accessories |  | Pressure tank Pressure sensor Terminal box Phase flange Foundation bolt Nameplate Other necessary accessories |

Note) Operation is to be performed alternately.

(5)	Water Intake Pump

(a)	Overview and Specifications

The water intake pump, which supplies water to the water tank, shall have the following specifications.

| Item |  | Specification |
| --- | --- | --- |
| Pump | Model | Submersible pump |
|  | Discharge rate | 90 l/min |
|  | Total pumping head | 114 m |
|  | Diameter | 40 A |
| Electric motor | Format | Water sealed three-phase induction motor |
|  | Rating | Continuous |
|  | Output | 5.5 kW |
|  | Rated voltage | 3φ 3W 200V |
|  | Rotational speed | 3000 rpm |
|  | Frequency | 50 Hz |
|  | Insulation type | Min. Class E |
|  | Activation method | Direct activation |
| Accessories |  | Compound pressure gauge Underwater cable Cable band Phase flange Nameplate Other necessary accessories |

(6)	Motorized Ball Valve (Inlet Valve)

(a)	Overview and Specifications

A discharge valve shall be installed to prevent the main distribution pipe from freezing. It shall have the following specifications.

| Item |  | Specification |
| --- | --- | --- |
| Valve body | Format | Flanged electric ball valve |
|  | Nominal diameter | 40A JIS10K FF |
|  | Material | Body-FC200 |
|  | Maximum working pressure | 1.37Mpa (14 kgf/cm2) |
| Electric motor | Format | 3-phase induction motor (4-pole) |
|  | Rating | 10 min. |
|  | Rated voltage | 200V |
|  | Frequency | 50 Hz |
|  | Output | 40 W |
|  | Torque | 125 N/m |
|  | Insulation class | Class E |
|  | Space heater | 8 W |

(7)	Automatic Air Vent Valve

(a)	Overview and Specifications

An automatic air vent valve shall be installed on piping to release air trapped when filling the distribution main pipe. It shall have the following specifications.

| Item | Specification |
| --- | --- |
| Format | Automatic Air Vent Valve |
| Nominal diameter | 20 A |
| Material | Pump room: CAC406 (main unit), SUS304 (float) Intake tank: SUS304 (main body), SUS304 (float) |
| Maximum working pressure | Pump room: 0.98 MPa (10 kgf/cm2) Intake tank:1.96 MPa (20 kgf/cm2) |

(8)	Safety Valve

(a)	Overview and Specifications

The safety valve is installed to prevent the pressure inside the main pipe from rising above a certain value. Its specifications shall be as follows.

| Item | Specification |
| --- | --- |
| Format | Safety Valve |
| Nominal diameter | 50 A |
| Material | Pump room: FC200 (body) Intake tank: SCPH2 (body) |
| Maximum working pressure | Pump room: 0.98 MPa (10 kgf/cm2) Intake tank:1.96 MPa (20 kgf/cm2) |

(9)	Flow Regulation Valve

(a)	Overview and Specifications

A flow regulation valve shall be installed for water intake of the distribution main to regulate the volume of water taken in. Its specifications shall be as follows.

| Item | Specification |
| --- | --- |
| Format | Flow Regulation Valve |
| Nominal diameter | 40 A |
| Material | Body: FC 200 |
| Maximum working pressure | 1.37 MPa (14 kgf/cm2) |
| Confined flow | 90 l/min |

(10)	Disaster Prevention Reception Panel

(a)	Overview

A disaster prevention reception panel (hereinafter, “disaster prevention panel”) displays the occurrence of a fire or similar disaster upon receiving a signal from a device such as a push button alarm, etc. It can start up firefighting equipment as well as sending signals to a remote supervisory control facility, ventilation equipment, warning display equipment, lighting equipment, CCTV equipment, and the like.

(b)	Applicable Legislation and Standards

- Japan Fire regulations and standards

- Japan Industrial Standard (JIS)

- Japanese Electrotechnical Committee standards (JEC)

- Japan Electrical Manufacturers' Association (JEM)

- Japan Electrical equipment technical standards

- Other relevant laws, regulations and standards

In addition to the above-mentioned items, equipment and facilities shall also conform to “Technical Standards Relating to Receivers” prescribed by ordinance of the Ministry of Internal Affairs and Communications of Japan.

Equivalent international standards will be allowed if duly justified by the Contractor, and approved by the Engineer.

(c)	General Matters

(i)	Indoor temperature and humidity

Temperature:  +5°C to +35°C

Humidity: Max. 85% (no condensation permitted)

- Model

Indoor freestanding enclosed type

(iii)	Structure

Material and thickness [Cold-reduced Carbon Steel Sheet and Strip (JIS G 3141)]

- Door:  minimum t3.2

- Side:  minimum t1.6

- Ceiling: minimum t1.6

Cable lead-in and feed-out methods

- In principle, cables shall be led-in/fed-out from under the board.

External wiring connection

- External wiring must be implemented accurately. Terminals, etc., shall be appropriate for the thickness, type and voltage of the wire to be connected, and not function abnormally when exposed to dust or moisture.

Doors and handles

- A hinged door with a lock shall be installed on the front and rear sides.

Equipment in the board

- Internal lighting (AC 100V fluorescent lighting)

Each hinged door shall be equipped with at least one light.

        - Lights shall automatically turn on or off when the door is opened or closed.

        - Outlet for internal inspection (AC 100V)

        - Phone: A telephone check for maintenance phones or plug-in phones shall be provided.

Circuit protection

- Power reception circuit: A surge absorber capable of withstanding an impulse current of at least 2,000A shall be installed between each line.

- I/O circuit (for emergency equipment installed in tunnel):  A surge absorber capable of withstanding an impulse current of at least 2,000A shall be installed between each signal line, common line, and line-to-ground. A protective circuit shall also be provided for each circuit to prevent a total board failure due to short-circuiting on the secondary side.

- Signal input circuit:  A variable type 1–15 second delay function shall be provided on push button alarms and fire hydrant activation signal circuits to provide time to determine if the signal was a malfunction caused by the lightning surge, etc.

(iv)	Electric system

The power receiving system shall be a dual power supply consisting of:

- an uninterruptible power supply (emergency power source) that receives power from emergency power supply equipment in the event of a commercial power outage, and

- general commercial power supply (for internal lighting, etc.).

The temporary power interruption time of the emergency power supply shall be no more than 250m.

The power receiving system shall be configured as follows:

- Emergency power supply:  AC single-phase two-wire, 100V ± 10%, 50 Hz

- General power supply: AC single-phase two-wire, 100V ± 10%, 50 Hz

Supplied Power: Power supply to monitoring equipment shall be as follows:

- Fire hydrant: DC 48V

- Fire detector: DC 48V

- Red signal light: AC single phase 2-wire, 100V ± 10%, 50 Hz

(v)	Grounding

The cabinet ground shall be Class D grounding at one location.

(vi)	Commercial frequency withstand voltage

100V circuit:  1,000V to ground

Circuits of 60V or less:  500V to ground

- However, the semiconductor applied circuit shall be short-circuited or separated.

(vii)	Wiring scheme

The wire type and color coating wire shall conform to standards of JEM 1425. However, the wire color coating does not need to follow this standard when using specialized insulated wire for the main circuit or when using specialized wires such as shielded wire. Further, this paragraph does not apply to the wiring of small circuits such as electronic circuits or the internal wiring of devices such as relays.

(viii)	Coating

Method:  Coating shall be a semi-gloss melamine baked enamel.

Coating color:  Munsell 5Y7/1.

(d)	Installation Location and Number of Panels

| Installation location | Number of panels |
| --- | --- |
| Communication equipment room | 1 |

(e)	Input Power

| Supply board | Voltage specification | Frequency | Remarks |
| --- | --- | --- | --- |
| Eastern communication room distribution board | AC 100V±10%，1φ2W | 50 Hz | Emergency power supply |
| Eastern Power Room House transformers (2) | AC 100V±10%，1φ2W |  | Miscellaneous power sources |

(f)	Functional Specifications

The following functions shall be provided:

Receive signals from fire detectors, circuit monitoring, detector testing

Receive signals from push button alarms, circuit monitoring.

Receive signals from fire hydrants and water supply outlets, circuit monitoring.

Receive signals from connection line to emergency tunnel door

Relay signals to the fire pump control board

Relay signals to the remote supervisory control facility

Send signals to ventilation control board

Send signals to lighting equipment

Send signals to CCTV equipment

Send signals to warning display panel

(g)	Monitoring Control System

The control and display functions shall be as follows.

(i)	Control

Control functions shall conform to the following table.

Note that in the following table, items listed as follows commands from remote supervisory control facility (hereinafter, “remote facility”) only apply if the remote facility has the function in question.

Control Functions and Methods - Part 1

| Control function | Control method | Content |
| --- | --- | --- |
| Operating location switchover “Remote (distant) –Direct (straight)” | Switched over on control unit | Remote: Remotely controls emergency equipment via commands from remote control facilities Direct: Directly control using the operating unit |
| Selection of control method “Auto–Manual” | Switched over on control unit or follows commands from remote facility | Auto: Starts firefighting pump in conjunction with the operation of other emergency equipment (fire hydrant, pump start push button, push button alarm system, fire detector). Manual: Starts firefighting pump in conjunction with operation of the operating unit or emergency equipment (excluding fire detector). Receives commands from remote facility and starts firefighting pump |
| Full recovery operation “Recover” | Push button on operating unit or follows commands from remote facility | When in automatic mode, restores emergency equipment, operating unit displays, and outputs to other equipment, and returns to a monitoring state. Note that failures are excluded. |
| Selection of interlocking method “Independent–Interlocked” | Switched over on control unit or follows commands from remote facility | Blocks fire signal output to the warning display panel |
| Blocks external signals “Block External Signals” | Push button on operating unit | Blocks the output to other equipment (automatic notification warning, preliminary warning, automatic warnings, automatic notice section, and manual notice section) except for to the pump control board and other disaster prevention panels. |

Control Functions and Methods - Part 2

| Control function |  | Control mode |  | Control method |
| --- | --- | --- | --- | --- |
|  |  | Automatic | Manual |  |
| Fire pump | Start (operate) | ○ | － | Operates in unison with fire hydrants, water supply outlets, push button alarm system, and fire detectors |
|  |  | － | ○ | Operates in unison with fire hydrants, water supply outlets, and push button alarm system |
|  |  | ○ | ○ | Operated by operating unit, or follows commands from remote facility |
|  | Stop | － | ○ | Operated by operating unit, or follows commands from remote facility |
|  |  | ○ | － | Operated by operating unit, or receives recovery commands from remote facility |

Control Functions and Methods - Part 3

| Control function |  | Control method |
| --- | --- | --- |
| System testing (Detector Test+Operation/Continuity Test) | Start | Follows commands from remote facility |
|  | Stop | Remote: Switched by the operating unit (remote → direct) or follows commands from remote facility Direct: Switched by the operating unit (direct → remote) or follows stop operation |
| Periodic system testing (Detector Test+Operation/Continuity Test) | Start | Automatically started from disaster prevention panel when in remote mode |
|  | Stop | Automatically stopped from disaster prevention panel when in remote mode |
| Detector test | Start | Operated by operating unit. Can only be started when in direct mode. |
|  | Stop | Direct: Switched by the operating unit (direct → remote) or follows stop operation |
| Operation/continuity test | Start | Operated by operating unit. Can only be started when in direct mode. |
|  | Stop | Direct: Switched by the operating unit (direct → remote) or follows recovery operation |

(ii)	Other notable matters

If only one fire detector has been triggered the status is set as “preliminary warning” and a preliminary warning signal shall be output to equipment except for radio rebroadcasting equipment, ventilation equipment and the warning display panel to call attention to the status.

If two or more fire detectors have been triggered, the status is set as “fire” and fire signal shall be output to all equipment.

The push button alarm system shall comprise direct/parallel circuits consisting of 'a' and 'b' contacts, and a warning shall be displayed if either are activated.

- The system should also be able to detect a disconnection or short-circuit as an abnormality in the push button circuit.

If a push button alarm has been sent or firefighting pump is activated, all red signal lights shall flash intermittently.

(h)	Board Display Items

In principle, the items to be displayed shall conform to the following table.

BL: Bell; BZ: Buzzer

| Control function |  | Control method |
| --- | --- | --- |
| System testing (Detector Test+Operation/Continuity Test) | Start | Follows commands from remote facility |
|  | Stop | Remote: Switched by the operating unit (remote → direct) or follows commands from remote facility Direct: Switched by the operating unit (direct → remote) or follows stop operation |
| Periodic system testing (Detector Test+Operation/Continuity Test) | Start | Automatically started from disaster prevention panel when in remote mode |
|  | Stop | Automatically stopped from disaster prevention panel when in remote mode |
| Detector test | Start | Operated by operating unit. Can only be started when in direct mode. |
|  | Stop | Direct: Switched by the operating unit (direct → remote) or follows stop operation |
| Operation/continuity test | Start | Operated by operating unit. Can only be started when in direct mode. |
|  | Stop | Direct: Switched by the operating unit (direct → remote) or follows recovery operation |

Items not listed above that are functionally required shall also be provided.

(i)	Board Operational Items

| Item | Number of items | Remarks |
| --- | --- | --- |
| Remote–Direct | 1 each |  |
| Auto–Manual | 1 each |  |
| Warning display panel, Independent–Interlocked | 1 each |  |
| Firefighting pump, Operate–Stop | 1 each |  |
| Recovery | 1 |  |
| Sound stop | 2 | Primary sound, failure alert sound |
| Block external signals | 1 |  |
| Test unit | 1 set | Including lamp testing |

Items not listed above that are functionally required shall also be provided.

(j)	Other Equipment Inputs and Outputs

Signals shall be relayed by a separately installed relay terminal board.

(i)	Remote supervisory control facility

Contact input specifications

| Contact method | Non-voltage 'a' contact method |
| --- | --- |
| Contact capacity | DC 24V, 50mA or more |
| Duration | 1 pulse signal per second, contact closes when there is a signal |

Controls from remote supervisory control facility

| Item | Number of items |
| --- | --- |
| Auto–Manual | 1 each |
| Fire detector test, Start-Stop | 1 each |
| Firefighting pump, Operate-Stop | 1 each |
| Warning display panel, Independent–Interlocked | 1 each |
| Recover | 1 |

Contact output specifications

| Contact method: | Non-voltage 'a' contact method |
| --- | --- |
| Contact capacity: | DC 24V or 48V，100mA or less |
| Duration: | Continuous signal, contact closes if signal present |

Outputs to remote supervisory control facility

| Item | Number of items | Remarks |
| --- | --- | --- |
| Disaster prevention panel: |  |  |
| direct (mode) | 1 |  |
| manual (mode) | 1 |  |
| Warning display panel, independent | 1 |  |
| Disaster prevention inspection in progress | 1 |  |
| Automatic notice section | 55 |  |
| Manual notice section | 14 |  |
| Automatic notification warning | 1 |  |
| Fire detector, preliminary warning | 1 |  |
| Fire hydrant, in use | 1 |  |
| Fire extinguishing pump: |  |  |
| independent | 1 |  |
| operating | 1 |  |
| failure | 1 |  |
| Automatic water supply system: |  |  |
| operating | 2 | No.1, No.2 |
| failure | 2 |  |
| abnormal pressure | 1 |  |
| Water intake pump |  |  |
| operating | 2 | No.1, No.2 |
| failure | 2 |  |
| Intake valve: |  |  |
| open | 1 |  |
| failure | 1 |  |
| Main water tank, water level | 3 | Overfilled, low water, dry |
| Intake tank, water level | 1 | Dry |
| Connection line to emergency tunnel door, open | 14 |  |
| Testing | 1 |  |
| Detector test: |  |  |
| fault detected unit number | 1 set | BCD code |
| contaminated | 1 |  |
| contamination warning | 1 |  |
| circuit failure | 1 |  |
| Manual alarm system, circuit failure | 1 |  |
| Fire hydrant, circuit disconnection | 1 |  |
| Connection line to emergency tunnel door, circuit disconnection | 1 |  |
| Fire detector, short-circuit | 1 |  |
| Disaster prevention panel, failure | 1 |  |
| Firefighting pump control board, failure | 1 |  |
| Water intake pump control board, failure | 1 |  |

Items not listed above that are functionally required shall also be provided.

(ii)	Other equipment

Contact output specifications

| Contact method: | Non-voltage 'a' contact method |
| --- | --- |
| Contact capacity: | DC 24V or 48V，100mA or less However, output to lighting only shall be DC 110V 100mA or less |
| Duration: | Continuous signal, contact closes if signal present |

Outputs to tunnel ventilation equipment from disaster prevention panel

| Item | No. of items | Remarks |
| --- | --- | --- |
| Automatic notice section | 1 | 2 or more detectors have been triggered |
| Manual notice section | 1 |  |

Outputs to warning display panel from disaster prevention panel

| Item | No. of items | Remarks |
| --- | --- | --- |
| Automatic notice section | 1 | 2 or more detectors have been triggered |
| Manual notice section | 1 |  |

Outputs to CCTV equipment from disaster prevention panel

| Item | No. of items | Remarks |
| --- | --- | --- |
| Automatic notice section | 55 | 1 or more detectors have been triggered |
| Manual notice section | 14 |  |

Outputs to lighting equipment from disaster prevention panel

| Item | No. of items | Remarks |
| --- | --- | --- |
| Automatic notice section | 1 | 1 or more detectors have been triggered |
| Manual notice section | 1 |  |

Outputs to rebroadcasting equipment (AM/FM shared) from disaster prevention panel

| Item | No. of items | Remarks |
| --- | --- | --- |
| Automatic notice section | 2 | 2 or more detectors have been triggered |
| Manual notice section | 2 |  |

(11)	Fire Pump Control Board

(a)	Overview

The fire pump control board receives signals from the disaster prevention panel, water level gauges, etc., and then controls various pumps and accessories and sends signals.

(b)	Applicable standards

Japanese Electricity Business Act

Japanese Electrical Appliance and Material Safety Law

Japanese Ministerial Ordinances that set technical standards related to electrical equipment

Japan Electrical Manufacturers' Association (JEM)

Japan Industrial Standard (JIS)

Equivalent international standards will be allowed if duly justified by the Contractor, and approved by the Engineer.

(c)	General Matters

(i)	Overload and open-phase protection devices shall be equipped for each motor. Overload and open-phase protection devices shall automatically prevent the occurrence of overcurrent due to overload or open phase, preventing motor burnout.

However, in the case of firefighting pumps, they shall not be halted due to failures from overload or open phase.

(ii)	Ammeters shall be extended scale ammeters (with red pointers) and be provided for each electric motor.

(iii)	Capacity of the leading power factor capacitor shall be selected as follows: for 200V motors it shall be selected based on power supply regulations of electric power companies; for 400V/high voltage motors it shall be selected such that power factor after improvement at the rated output is at least 90%.

(iv)	Operating and stopped status indicator lights shall be provided for each motor, and protective relay operational indicators shall be provided for each protective relay.

(v)	Model: Indoor freestanding enclosed type

(vi)	Structure

Material and thickness [Cold-reduced Carbon Steel Sheet and Strip (JIS G 3141)]

- Door: 	minimum t3.2

- Side plate:	minimum t1.6

- Ceiling plate:	minimum t1.6

Lead-in and feed-out methods:  In principle, cables shall be led-in/fed-out from under the board.

Doors and handles

- Freestanding types shall have a hinged door on the front.

- The opening direction shall be either left hinge (right handle) or right hinge (left handle) and those lined-up in the same row of a board shall all be consistent in configuration and opening direction.

- The handle rotating direction shall be as follow:

- Left hinged: 	Door opens by turning the handle clockwise.

- Right hinged: 	Door opens by turning the handle counterclockwise.

- Door handles shall have a key lock, using Takigen model A-140 (key, No.200).

(vii)	Equipment in the board

Internal lighting (AC 100V fluorescent lighting)

- Each hinged door shall be equipped with at least one light.

- Lights shall automatically turn on or off when the door is opened or closed.

Outlet for internal inspection (AC 100V)

(viii)	Coating

Substrate treatment: Parkerizing

Undercoating:

- 1 coat of melamine primer

- 1 coat of melamine surface coating

Top coating: 2 coats of melamine resin baked enamel

Coating color: Munsell 5Y7/1 semi-gloss (both inside and outside)

Thickness: 40 μm minimum

(d)	Installation Location and Number of Panels

| Installation location | No. of panels |
| --- | --- |
| Pump room | 1 |

(e)	Input Power

| Supply board | Voltage specification | Frequency | Remarks |
| --- | --- | --- | --- |
| Eastern Power Room Maintenance switching No.1 | AC415V±10％，3φ3W | 50 Hz | In-house power generation circuit |
| Eastern Power Room Maintenance switching No.2 | AC210V±10％，3φ3W |  |  |

(f)	Load Capacity

| Load | Voltage specification | Load Capacity | Remarks |
| --- | --- | --- | --- |
| Fire pump | AC 400V | 22 kW | Star-delta starting |
| Automatic Water Supply System | AC200V | 0.4 kW×2 | Full-voltage starting |
| Intake valve |  | 0.04 kW |  |
| Heater to prevent condensation |  | 0.05 kW | Fire pump |
| Control circuit |  | 0.3 kVA |  |
| Miscellaneous power sources |  | 0.6 kVA |  |

However, the automatic water supply system and intake pump shall be operated by automatically alternating.

(g)	Monitoring method

(i)	Control mode

Firefighting pump start/stop is controlled by a signal from the disaster prevention panel

Each pump's start/stop is controlled by a push button switch on the control board.

Each valve's open/close is controlled by a push button switch on the control board.

(ii)	Display method: Display shall be illuminating type.

(iii)	Board mounted equipment

Operation

- “Independent–Interconnected” switchover switch

- Pump 'Operate–Stop' push button switch

- Valve 'open-close' push button switch

Display

- Instruments (ammeter, voltmeter, hour meter)

- Status indicator lamps for various board mounted operating switches

- Status indicator lamps for fires, various pumps, and water level.

Items not listed above that are functionally required shall also be provided.

(h)	Monitoring Control Items

| Item Type | Control | Display | Remarks |
| --- | --- | --- | --- |
| Fire | － | 1 |  |
| Firefighting pump: |  |  |  |
| - Independent–Interconnected | 1 | 1 each |  |
| - operate–stop | 1 each | 1 each |  |
| - failure | － | 1 |  |
| Automatic water supply system: |  |  |  |
| - Auto–Manual | 1 | 1 each |  |
| - operate–stop | 2 each | 2 each | No.1, No.2 |
| - failure | － | 2 | No.1, No.2 |
| - abnormal pressure | － | 1 |  |
| Water intake pump, independent | － | 1 |  |
| Water intake pump: |  |  |  |
| - Auto–Manual | 1 | 1 each |  |
| - operate–stop | 1 each | 1 each |  |
| - failure | － | 2 | No.1, No.2 |
| Water intake valve: |  |  |  |
| - Auto–Manual | 1 | 1 each |  |
| - open–close | 1 each | 1 each |  |
| - failure | － | 1 |  |
| Main water tank, water level | － | 6 | Overfilled, standard level, low water, dry Water intake pump, Operate–Stop |
| Intake tank, water level | － | 1 | Dry |
| Fire hydrant, in use | － | 1 |  |
| Firefighting pump control board, failure | － | 1 |  |
| Water intake pump control board, failure | － | 1 |  |
| Power supply | － | 1 |  |
| Sound stop | － | 1 |  |
| Lamp test | 1 | － |  |
| Temperature control | 1 | － |  |
| Pressure regulator | 1 | － |  |

Items not listed above that are functionally required shall also be provided.

(i)	Signal Relay with Other Equipment

(i)	Disaster Prevention Reception Panel

Contact input specifications

| Contact method: | Non-voltage 'a' contact method |
| --- | --- |
| Contact capacity: | DC 24V or 48V, 50mA or over |
| Duration: | Continuous signal, contact closes if signal present |

Inputs from disaster prevention panel

| Item | No. of items |
| --- | --- |
| Fire | 1 |
| Firefighting pump: |  |
| - operate command | 1 |
| - Stop command | 1 |
| Fire hydrant, in use | 1 |

Contact output specifications

| Contact method: | Non-voltage 'a' contact method |
| --- | --- |
| Contact capacity: | DC 24V or 48V，100mA or less |
| Duration: | Continuous signal, contact closes if signal present |

Outputs to disaster prevention panel

| Item | Number of items | Remarks |
| --- | --- | --- |
| Fire extinguishing pump: |  |  |
| - independent | 1 |  |
| - operating | 1 |  |
| - failure | 1 |  |
| Automatic water supply system: |  |  |
| - operating | 2 | No.1, No.2 |
| - failure | 2 | No.1, No.2 |
| - abnormal pressure | 1 |  |
| Water intake pump: |  |  |
| - operating | 2 | No.1, No.2 |
| - failure | 2 | No.1, No.2 |
| Intake valve: |  |  |
| - open | 1 |  |
| - failure | 1 |  |
| Main water tank, water level | 5 | Overfilled, low water, dry Water intake pump, Operate–Stop |
| Intake tank, water level | 1 | Dry |
| Water distribution system, checking | 1 |  |
| Firefighting pump control board, failure | 1 |  |
| Water intake pump control board, failure | 1 |  |

Items not listed above that are functionally required shall also be provided.

(12)	Water Intake Pump Control Board

(a)	Overview

The water intake pump control board receives signals from the fire fighting pump control board, and controls pumps and sends signals to the main tank to maintain water supply.

(b)	Applicable standards

Japanese Electricity Business Act

Japanese Electrical Appliance and Material Safety Law

Japanese Ministerial Ordinances that set technical standards related to electrical equipment

Japan Electrical Manufacturers' Association (JEM)

Japan Industrial Standard (JIS)

Equivalent international standards will be allowed if duly justified by the Contractor, and approved by the Engineer.

(c)	General Matters

(i)	Overload and open-phase protection devices shall be equipped for each motor. Overload and open-phase protection devices shall automatically prevent the occurrence of overcurrent due to overload or open phase, preventing motor burnout.

(ii)	Ammeters shall be extended scale ammeters (with red pointers) and be provided for each electric motor.

(iii)	For 200V motors, capacity of the leading power factor capacitor shall be selected based on power supply regulations of electric power companies.

(iv)	Operating and stopped status indicator lights shall be provided for each motor, and protective relay operational indicators shall be provided for each protective relay.

(v)	Model: Outdoor standing type

(vi)	Structure

Material and thickness [Cold-reduced Carbon Steel Sheet and Strip (JIS G 3141)]

- Outdoor standing type

- Door:  minimum t2.3

- Side plate: minimum t2.3

- Ceiling plate: minimum t2.3

Lead-in and feed-out methods:  In principle, cables shall be led-in/fed-out from under the board.

Doors and handles:  A hinged door with a lock shall be installed on the front.

(vii)	Equipment in the board

Internal lighting (AC 100V fluorescent lighting)

- For freestanding types, each hinged door shall be equipped with at least one light.

- Lights shall automatically turn on or off when the door is opened or closed.

Outlet for internal inspection (AC 100V)

(viii)	Coating: Finishing shall be zinc hot-dip galvanizing (HDZ35)

(d)	Installation Location and Number of Panels

| Installation location | No. of panels |
| --- | --- |
| Naubise entrance | 1 |

(e)	Input Power

| Supply board | Voltage specification | Frequency |
| --- | --- | --- |
| Western Power Room Maintenance switching No.2 | AC210V±10%，3φ3W | 50 Hz |

(f)	Load Capacity

| Load | Voltage specification | Load Capacity | Remarks |
| --- | --- | --- | --- |
| Water intake pump | AC200V | 5.5 kW×2 | Full-voltage starting |
| Control circuit |  | 0.3 kVA |  |
| Miscellaneous power sources |  | 0.6 kVA |  |

However, the water intake pump shall be operated by automatically alternating.

(g)	Monitoring method

(i)	Control mode

Water intake pump start/stop is controlled by the signal from the firefighting pump control board.

Water intake pump start/stop is controlled by a push button switch on the control board.

(ii)	Display method:  Display shall be illuminating type.

(iii)	Board mounted equipment

Operation

- “Independent–Interconnected” switchover switch

- Pump 'Operate–Stop' push button switch

Display

- Instruments (ammeter, voltmeter, hour meter)

- Status indicator lamps for various board mounted operating switches

- Status indicator lamps for fires and various pumps

Items not listed above that are functionally required shall also be provided.

(h)	Monitoring Control Items

| Item Type | Control | Display | Remarks |
| --- | --- | --- | --- |
| Fire | － | 1 |  |
| Firefighting pump, operating | － | 1 |  |
| Water intake pump: |  |  |  |
| - Independent–Interconnected | 1 | 1 each |  |
| - operate–stop | 2 each | 2 each | No.1, No.2 |
| - failure | － | 2 | No.1, No.2 |
| Water intake pump control board, failure | － | 1 |  |
| Intake tank, water level | － | 1 | Dry |
| Power supply | － | 1 |  |
| Lamp test | 1 | － |  |

Items not listed above that are functionally required shall also be provided.

(i)	Signal Relay with Other Equipment

(i)	Fire pump control board

Contact input specifications

| Contact method: | Non-voltage 'a' contact method |
| --- | --- |
| Contact capacity: | DC 24V or 48V, 50mA or over |
| Duration: | Continuous signal, contact closes if signal present |

Inputs from the firefighting pump control board

| Item | No. of items |
| --- | --- |
| Fire | 1 |
| Firefighting pump: |  |
| - operating | 1 |
| Water intake pump: |  |
| - operate command | 1 |
| - stop command | 1 |

Contact output specifications

| Contact method: | Non-voltage 'a' contact method |
| --- | --- |
| Contact capacity: | DC 24V or 48V，100mA or less |
| Duration: | Continuous signal, contact closes if signal present |

Outputs to the firefighting pump control board

| Item | No. of items | Remarks |
| --- | --- | --- |
| Water intake pump: |  |  |
| - independent | 1 |  |
| - operating | 2 | No.1, No.2 |
| - failure | 2 | No.1, No.2 |
| Intake tank, water level | 1 | Dry |
| Water intake pump control board, failure | 1 |  |

Items not listed above that are functionally required shall also be provided.

(13)	Terminal Board

(a)	Overview

The terminal board relays the electrical circuits of equipment in the tunnel.

(b)	General Matters

(i)	Model:  Outdoor wall-embedded type

(ii)	Structure

Structure:  The terminal board shall have a double structure comprising an inner box and outer box. The front panel of the outer box shall be fastened with stainless steel bolts.

Material and thickness:  Cold-rolled Stainless Steel Plate, Sheet and Strip (JIS G 4305), minimum t1.5

Waterproof (inner box only):  Jetproof structure JIS C 0920

- (Degrees of Protection Provided by Enclosures)

Heat resistance:  Insulation (of rock wool at least 25 mm thick) shall be fitted on the inside of the outer box (excluding the back surface) to provide heat resistance.

(iii)	Coating: Based on consultation with the contracting party.

(14)	Fire Detectors

(a)	Overview

Fire detectors automatically detect fires that break out in the tunnel and notify the Disaster Prevention Panel of its location.

(b)	Applicable Legislation and Standards

Japan Fire regulations and standards

Japan Industrial Standard (JIS)

Japan Electrical equipment technical standards

Equivalent international standards will be allowed if duly justified by the Contractor, and approved by the Engineer.

(c)	General Matters

(i)	Ambient temperature:  -20°C to +50°C.

(ii)	Detection method:  Dual-wavelength flicker detection method

(iii)	Method:  Direct sending (P) method

(iv)	Structure

Material and thickness

- Fire detector body: Aluminum Alloy Die Castings（JIS H 5302）ADC12

- Fire detector box, front plate, shade plate

Cold-rolled Stainless Steel Plate, Sheet and Strip (JIS G 4305), minimum t1.2

Light sensor window:  The light sensor window shall have a streamlined shape that resists adhesion of suspended pollutants to reduce the amount of contamination that adheres to it.

Waterproofing

- Watertight structure JIS C 0920

- (Degrees of Protection Provided by Enclosures)

(v)	Electric system

Power supply voltage:  DC 48V（＋10％，－20％）

Current consumption

- When monitoring:  13 mA

- When operating:  35 mA

- When testing:  50 mA

(vi)	Coating:  Based on consultation with the contracting party.

(d)	Functions

(i)	Fire detection:  Opposing view commonality detection

(ii)	Monitoring range and sensitivity:  Within a 0-85% sensor contamination rate, the fire detector shall can detect a 0.5m2 (0.7×0.7 m flash pan) gasoline fire (2 l or more of vehicle gasoline) within 50 m at 90°to its left and right and 20m in front (max. distance in the diagonal direction is 53.9 m) and activate within 30 seconds. Wind speed when burning shall be no more than 12 m/sec.

(iii)	Non-activating conditions:  The detector shall not activate under the following conditions subjected to its sensor window.

5000 lx incandescent light bulb with a filament temperature of 2856±50 K

10,000 lx sodium light

10,000 lx fluorescent light

10,000 lx natural light

1,000 lx revolving light (yellow, red, blue, green, violet)

(iv)	Functionality testing:  Detectors shall have a function allows them to be tested from the disaster prevention panel while being installed in the tunnel.

(v)	Operation check: It must be possible to visually check if a detector is operating by the presence of an LED light etc.

- LED:  Red, green (2 on each left and right)

- Normal monitoring:  Lights off

- Triggered:  Red LED brightly flashes intermittently

- After being triggered:  Red LED dimly flashes intermittently

- When testing:  Green LED flashes intermittently

(vi)	Contaminated/inoperative signal output: A signal shall be sent to warn when optical light has fallen below 85%. Further, a contamination warning signal shall be sent when optical light has fallen below 75%.

(vii)	Contamination compensation:  Detector sensitivity shall automatically compensate for sensor window contamination based on the light sensor window contamination measurement in the detector test. The detector shall can maintain the prescribed sensitivity up to an 85% contamination rate (optical light reduction rate).

(viii)	Self shutdown

To protect against powerful surges, detectors shall be equipped with resistive protection that acts as a fuse to avoid adverse impact on the system caused by a short circuit, etc., of electronic parts.

In the unlikely event that an overcurrent occurs in the internal circuit, the protective resistor will open, causing the detector to shut itself down and output a failure signal.

(ix)	Self-diagnosis:  Even during normal monitoring and detector testing, the detector shall perform a self-diagnosis of its circuits and output a circuit failure signal if a circuit failure is detected.

(15)	Push Button Alarms (In Emergency Phone Boxes)

(a)	Overview and Configuration

A push button alarm shall be installed in every emergency phone box with the following configuration.

| Component | Quantity |
| --- | --- |
| Cabinet box | 1 set |
| Push button alarm | 1 pc. |
| Telephone jack | 1 pc. |
| Circuit terminal | 1 set |
| Equipment name plate | 1 set |

(b)	Specifications

(i)	Cabinet box

Material:  SPCC t1.6

Coating:  Heat cured epoxy powder coating (Munsell 7.1R 3.6/12.8)

(ii)	Push button alarm: The push button notification system shall conform to the standards set by the Ministry of Home Affairs for P-type Grade 1 Transmitting Devices, and shall be constructed with a jetproof push button switch.

Transmitter body

- Material

① Body: SUS304

② Acrylic glass: Methacrylic resin

- Coating

① Front: Heat cured epoxy powder coating (Munsell 7.1R 3.6/12.8)

Push button switch

- Name:   Non-locking push button switch

- Contact rating:   AC 110V/DC 110V 5A/2.2A

- Contact configuration:  1a, 1b

(iii)	Telephone jack:  Shall be of a jetproof structure.

Name:  Plug-in telephone jack

Standard:  Japan Fire Alarms Manufacturer's Association, Unified Standard

- (equivalent to the Defense Agency old standard JJ-033)

(iv)	Circuit terminal

Material:  Synthetic resin

(v)	Equipment name plate

Material:   Methacrylic resin

Lettering:   Florescent red

(16)	Pump Start Push Button Box

(a)	Overview and Configuration

The pump start push button box shall have the following configuration.

| Component | Quantity |
| --- | --- |
| Cabinet box | 1 set |
| Pump start push button | 1 pc. |
| Telephone jack | 1 pc. |
| Circuit terminal | 1 set |
| Equipment name plate | 1 set |

(b)	Specifications

(i)	Cabinet box [Cold-rolled Stainless Steel Plate, Sheet and Strip (JIS G 4305)]

Material:  minimum t1.2

Coating:  Based on consultation with the contracting party.

(ii)	Pump start push button

Type:  Jetproof structure with non-locking push button switch

Contact rating:  AC 110V/DC 110V 5A/2.2A

Contact configuration:  1a

(iii)	Telephone jack: Shall be of a jetproof structure.

Name:   Plug-in telephone jack

Standard:   Japan Fire Alarms Manufacturer's Association, Unified Standard

- (equivalent to the Defense Agency old standard JJ-033)

(iv)	Circuit terminal

Material:   Synthetic resin

(v)	Equipment name plate

Material: 	Methacrylic resin

Lettering: 	Black on white background

5700.	DISTRIBUTION LINE

(1)	Description

This product is a tube for protecting the cable inside the tunnel. Since it has a rectangular structure, it has high external pressure strength and position stability is good when laying multiple stages, so that a nozzle stand like a cylindrical tube becomes unnecessary and it is possible to compactly form a multi-channel line, Since the pipe is in close contact with the pipe, backfilling is very easy and curved piping is also easy. In addition, since the pipe material is lightweight and has flexibility, it has good workability, has high water barrier against external water pressure, and has low wire resistance

(2)	Basic  Requirement

Protective tubes shall meet the following criteria

| Item | Characteristic value |
| --- | --- |
| Density(kg/m3) | 942 more |
| Tensile yield stress(MPa) | 19.6 more |

5800.	MEASUREMENT AND PAYMENT

(1)	Measurement

The works for the Tunnel Facilities shall be measured in lump sum but summarized in each Sub-Section herein described, prorating the actually provided and installed items against the total of each Sub-Section shown here below.  The items to be counted shall be only those duly installed, tested in accordance with the requirements of this Specifications, and approved by the Engineer.

For final measurement, each Sub-Item shall be measured counting only the items that have been satisfactorily tested according to the Quality Control and Commissioning herein described, and in accordance with Clause 509(3): “Testing and Commissioning” and conforming the requirements of Clause 9: “Test on Completion” of the Conditions of Contract, and after confirmation of proper function of the established system, satisfying all requirements of these Specifications, in accordance with the Drawings, and approved by Engineer.

(2)	Payment

The works for the Tunnel Facilities, measured as described above, shall be paid under this Section in lump sum which shall be the full and the final compensation to the Contractor as per Clause 112 including the cost for Design Review and Updating, provision of all materials, equipment, all operations required for construction as shown in the Drawings and described in this Item including drawings, tests, cabling, civil works and all other ancillary works and any incidental work needed to complete the work as per these Specifications and/or directed by the Engineer.

| Item No. | Description | Unit |
| --- | --- | --- |
| 5000 | Tunnel Facilities |  |
| 5100 | Tunnel Power Supply System | lump sum |
| 5200 | Tunnel Lighting System | lump sum |
| 5300 | Tunnel Emergency Facilities | lump sum |
| 5400 | Remote Monitoring And Control System | lump sum |
| 5500 | Tunnel Ventilation System | lump sum |
| 5600 | Tunnel Fire Fighting System | lump sum |
| 5700 | Tunnel Distribution line | lump sum |

5100  Tunnel Power Supply System

(1) Power Receiving & Distribution Facility (East Electric Room)

(2)	Power Receiving & Distribution Facility (West Electric Room)

(3)	Generator Facility

5200 Tunnel Lighting System

5300  Tunnel Emergency Facilities

5400  Tunnel Monitoring and Control System

(1)  Monitoring control

(2)	Radio Rebroadcasting System & Wireless Communication System

(3)	Closed Circuit Television System

5500  Tunnel  Ventilation  System

5600  Tunnel  Fire Fighting System

5700　Tunnel Distribution Line